## Transformers
Name	Technology	Rated power [MVA]	Nominal Frequency [Hz]	HV[kV]	LV[kV]	Positive sequence Short circuit voltage [%]	Copper losses [%]	Zero sequence Short circuit voltage [%]	Ratio X/R	x1 [p.u.]	r1 [p.u.]	HV vector group	LV vector group	Internal Delta Winding	Phase shift [Deg * 30º]	Name	uk0	Re(uk0)	Ratio X0/R0	x0	r0
															*30deg		%	%		p.u.	p.u.
0.01 MVA 10/0.4 kV DT 10 SGB	Three Phase Transformer	0.01	50	10	0.4	4	0.35	3.5	0.5532833	0.01936491	0.035	Y	ZN	0	5	Yzn5	4	3.5	0.5532833	0.01936491	0.035
0.016 MVA 10/0.4 kV DT 16 SGB	Three Phase Transformer	0.016	50	10	0.4	4	0.45	2.8125	1.011294	0.02844265	0.028125	Y	ZN	0	5	Yzn5	4	2.8125	1.011294	0.02844265	0.028125
0.016 MVA 10/0.4 kV ET 16 SGB	Three Phase Transformer	0.016	50	10	0.4	3.75	0.45	2.8125	0.8819174	0.02480392	0.028125	Y	ZN	0	5	Yzn5	3.75	2.8125	0.8819172	0.02480392	0.028125
0.016 MVA 10/0.4 kV ET 16/23 SGB	Three Phase Transformer	0.016	50	10	0.4	3.75	0.45	2.8125	0.8819174	0.02480392	0.028125	Y	ZN	0	5	Yzn5	3.75	2.8125	0.8819172	0.02480392	0.028125
0.025 MVA 10/0.4 kV DT 25 SGB	Three Phase Transformer	0.025	50	10	0.4	4	0.7	2.8	1.020204	0.02856571	0.028	Y	ZN	0	5	Yzn5	4	2.8	1.020204	0.02856571	0.028
0.025 MVA 10/0.4 kV ET 25 SGB	Three Phase Transformer	0.025	50	10	0.4	3.75	0.55	2.2	1.38039	0.03036857	0.022	Y	ZN	0	5	Yzn5	3.75	2.2	1.38039	0.03036857	0.022
0.025 MVA 10/0.4 kV ET 25/23 SGB	Three Phase Transformer	0.025	50	10	0.4	3.75	0.55	2.2	1.38039	0.03036857	0.022	Y	ZN	0	5	Yzn5	3.75	2.2	1.38039	0.03036857	0.022
0.04 MVA 10/0.4 kV DT 40 SGB	Three Phase Transformer	0.04	50	10	0.4	4	0.9	2.25	1.469862	0.03307189	0.0225	Y	ZN	0	5	Yzn5	4	2.25	1.469862	0.03307189	0.0225
0.04 MVA 10/0.4 kV ET 40 SGB	Three Phase Transformer	0.04	50	10	0.4	3.75	0.75	1.875	1.732051	0.03247595	0.01875	Y	ZN	0	5	Yzn5	3.75	1.875	1.732051	0.03247595	0.01875
0.04 MVA 10/0.4 kV ET 40/23 SGB	Three Phase Transformer	0.04	50	10	0.4	3.75	0.75	1.875	1.732051	0.03247595	0.01875	Y	ZN	0	5	Yzn5	3.75	1.875	1.732051	0.03247595	0.01875
0.05 MVA 10/0.4 kV 0.22 GEAFOL	Three Phase Transformer	0.05	50	10	0.4	4	1.05	2.1	1.621147	0.03404409	0.021	D	YN	0	5	Dyn5	4	2.1	1.621147	0.03404409	0.021
0.05 MVA 10/0.4 kV 0.28 GEAFOL	Three Phase Transformer	0.05	50	10	0.4	4	1	2	1.732051	0.03464102	0.02	D	YN	0	5	Dyn5	4	2	1.732051	0.03464102	0.02
0.05 MVA 10/0.4 kV DTTHL SGB	Three Phase Transformer	0.05	50	10	0.4	4	1.3	2.6	1.16913	0.03039737	0.026	Y	ZN	0	5	Yzn5	4	2.6	1.16913	0.03039737	0.026
0.063 MVA 10/0.4 kV DT 63 SGB	Three Phase Transformer	0.063	50	10	0.4	4	1.2	1.904762	1.846618	0.03517368	0.01904762	Y	ZN	0	5	Yzn5	4	1.904762	1.846618	0.03517368	0.01904762
0.063 MVA 10/0.4 kV DT 63/10 F SGB	Three Phase Transformer	0.063	50	10	0.4	4	1.35	2.142857	1.576212	0.03377597	0.02142857	Y	ZN	0	5	Yzn5	4	2.142857	1.576212	0.03377597	0.02142857
0.063 MVA 10/0.4 kV DTKa 3.8 SGB	Three Phase Transformer	0.063	50	10	0.4	3.8	1.4	2.222222	1.387119	0.03082487	0.02222222	Y	ZN	0	5	Yzn5	3.8	2.222222	1.387119	0.03082487	0.02222222
0.063 MVA 10/0.4 kV DTKa 4 SGB	Three Phase Transformer	0.063	50	10	0.4	4	1.4	2.222222	1.496663	0.03325918	0.02222222	Y	ZN	0	5	Yzn5	4	2.222222	1.496663	0.03325918	0.02222222
0.063 MVA 10/0.4 kV ET 63 SGB	Three Phase Transformer	0.063	50	10	0.4	3.75	1.05	1.666667	2.015565	0.03359274	0.01666667	Y	ZN	0	5	Yzn5	3.75	1.666667	2.015564	0.03359274	0.01666667
0.063 MVA 10/0.4 kV ET 63/23 SGB	Three Phase Transformer	0.063	50	10	0.4	3.75	1.05	1.666667	2.015565	0.03359274	0.01666667	Y	ZN	0	5	Yzn5	3.75	1.666667	2.015564	0.03359274	0.01666667
0.075 MVA 10/0.4 kV 0.28 GEAFOL	Three Phase Transformer	0.075	50	10	0.4	4	1.35	1.8	1.984508	0.03572114	0.018	D	YN	0	5	Dyn5	4	1.8	1.984508	0.03572114	0.018
0.075 MVA 10/0.4 kV 0.36 GEAFOL	Three Phase Transformer	0.075	50	10	0.4	4	1.35	1.8	1.984508	0.03572114	0.018	D	YN	0	5	Dyn5	4	1.8	1.984508	0.03572114	0.018
0.1 MVA 10/0.4 kV 0.27 GEAFOL	Three Phase Transformer	0.1	50	10	0.4	6	1.7	1.7	3.384782	0.05754129	0.017	D	YN	0	5	Dyn5	6	1.7	3.384782	0.05754129	0.017
0.1 MVA 10/0.4 kV 0.44 GEAFOL	Three Phase Transformer	0.1	50	10	0.4	4	1.6	1.6	2.291288	0.0366606	0.016	D	YN	0	5	Dyn5	4	1.6	2.291288	0.0366606	0.016
0.1 MVA 10/0.4 kV 4 GEAFOL	Three Phase Transformer	0.1	50	10	0.4	4	1.7	1.7	2.129866	0.03620773	0.017	D	YN	0	5	Dyn5	4	1.7	2.129866	0.03620773	0.017
0.1 MVA 10/0.4 kV 6 GEAFOL	Three Phase Transformer	0.1	50	10	0.4	6	1.7	1.7	3.384782	0.05754129	0.017	D	YN	0	5	Dyn5	6	1.7	3.384782	0.05754129	0.017
0.1 MVA 10/0.4 kV DOTE 100/10 SGB	Three Phase Transformer	0.1	50	10	0.4	4	1.75	1.75	2.055356	0.03596874	0.0175	Y	ZN	0	5	Yzn5	4	1.75	2.055356	0.03596874	0.0175
0.1 MVA 10/0.4 kV DOTEL 100/10 SGB	Three Phase Transformer	0.1	50	10	0.4	4	1.75	1.75	2.055356	0.03596874	0.0175	Y	ZN	0	5	Yzn5	4	1.75	2.055356	0.03596874	0.0175
0.1 MVA 10/0.4 kV DOTN 100/10 SGB	Three Phase Transformer	0.1	50	10	0.4	4	2.15	2.15	1.568863	0.03373055	0.0215	Y	ZN	0	5	Yzn5	4	2.15	1.568863	0.03373055	0.0215
0.1 MVA 10/0.4 kV DOTNL 100/10 SGB	Three Phase Transformer	0.1	50	10	0.4	4	2.15	2.15	1.568863	0.03373055	0.0215	Y	ZN	0	5	Yzn5	4	2.15	1.568863	0.03373055	0.0215
0.1 MVA 10/0.4 kV DT 100 SGB	Three Phase Transformer	0.1	50	10	0.4	4	1.7	1.7	2.129866	0.03620773	0.017	Y	ZN	0	5	Yzn5	4	1.7	2.129866	0.03620773	0.017
0.1 MVA 10/0.4 kV DT 100/10 F SGB	Three Phase Transformer	0.1	50	10	0.4	4	1.7	1.7	2.129866	0.03620773	0.017	Y	ZN	0	5	Yzn5	4	1.7	2.129866	0.03620773	0.017
0.1 MVA 10/0.4 kV DTKa 3.8 SGB	Three Phase Transformer	0.1	50	10	0.4	3.8	1.85	1.85	1.794196	0.03319262	0.0185	Y	ZN	0	5	Yzn5	3.8	1.85	1.794196	0.03319262	0.0185
0.1 MVA 10/0.4 kV DTKa 4 SGB	Three Phase Transformer	0.1	50	10	0.4	4	1.95	1.95	1.791021	0.03492492	0.0195	Y	ZN	0	5	Yzn5	4	1.95	1.791021	0.03492492	0.0195
0.1 MVA 10/0.4 kV DTTHL SGB	Three Phase Transformer	0.1	50	10	0.4	4	2.1	2.1	1.621147	0.03404409	0.021	Y	ZN	0	5	Yzn5	4	2.1	1.621147	0.03404409	0.021
0.1 MVA 10/0.4 kV Dyn1 ASEA	Three Phase Transformer	0.1	50	10	0.4	4	1.7	1.7	2.129866	0.03620773	0.017	D	YN	0	1	Dyn1	4	1.7	2.129866	0.03620773	0.017
0.1 MVA 10/0.4 kV Dyn1 wnr ASEA	Three Phase Transformer	0.1	50	10	0.4	4	1.7	1.7	2.129866	0.03620773	0.017	D	YN	0	1	Dyn1	4	1.7	2.129866	0.03620773	0.017
0.1 MVA 10/0.4 kV Dyn11 ASEA	Three Phase Transformer	0.1	50	10	0.4	4	1.7	1.7	2.129866	0.03620773	0.017	D	YN	0	11	Dyn11	4	1.7	2.129866	0.03620773	0.017
0.1 MVA 10/0.4 kV Dyn11 wnr ASEA	Three Phase Transformer	0.1	50	10	0.4	4	1.7	1.7	2.129866	0.03620773	0.017	D	YN	0	11	Dyn11	4	1.7	2.129866	0.03620773	0.017
0.1 MVA 10/0.4 kV Dyn5 ASEA	Three Phase Transformer	0.1	50	10	0.4	4	1.7	1.7	2.129866	0.03620773	0.017	D	YN	0	5	Dyn5	4	1.7	2.129866	0.03620773	0.017
0.1 MVA 10/0.4 kV Dyn5 wnr ASEA	Three Phase Transformer	0.1	50	10	0.4	4	1.7	1.7	2.129866	0.03620773	0.017	D	YN	0	5	Dyn5	4	1.7	2.129866	0.03620773	0.017
0.1 MVA 10/0.4 kV Dyn7 ASEA	Three Phase Transformer	0.1	50	10	0.4	4	1.7	1.7	2.129866	0.03620773	0.017	D	YN	0	7	Dyn7	4	1.7	2.129866	0.03620773	0.017
0.1 MVA 10/0.4 kV Dyn7 wnr ASEA	Three Phase Transformer	0.1	50	10	0.4	4	1.7	1.7	2.129866	0.03620773	0.017	D	YN	0	7	Dyn7	4	1.7	2.129866	0.03620773	0.017
0.1 MVA 10/0.4 kV ET 100 SGB	Three Phase Transformer	0.1	50	10	0.4	3.75	1.5	1.5	2.291288	0.03436932	0.015	Y	ZN	0	5	Yzn5	3.75	1.5	2.291288	0.03436932	0.015
0.1 MVA 10/0.4 kV ET 100/23 SGB	Three Phase Transformer	0.1	50	10	0.4	3.75	1.5	1.5	2.291288	0.03436932	0.015	Y	ZN	0	5	Yzn5	3.75	1.5	2.291288	0.03436932	0.015
0.1 MVA 10/0.4 kV Trafo Union	Three Phase Transformer	0.1	50	10	0.4	4	1.9	1.9	1.852602	0.03519943	0.019	Y	ZN	0	5	Yzn5	4	1.9	1.852602	0.03519943	0.019
0.1 MVA 10/0.4 kV Trafo Union wnr	Three Phase Transformer	0.1	50	10	0.4	4	1.9	1.9	1.852602	0.03519943	0.019	Y	ZN	0	5	Yzn5	4	1.9	1.852602	0.03519943	0.019
0.1 MVA 10/0.4 kV Yyn0 ASEA	Three Phase Transformer	0.1	50	10	0.4	4	1.7	1.7	2.129866	0.03620773	0.017	Y	YN	0	0	Yyn0	4	1.7	2.129866	0.03620773	0.017
0.1 MVA 10/0.4 kV Yyn0 wnr ASEA	Three Phase Transformer	0.1	50	10	0.4	4	1.7	1.7	2.129866	0.03620773	0.017	Y	YN	0	0	Yyn0	4	1.7	2.129866	0.03620773	0.017
0.1 MVA 10/0.4 kV Yyn6 ASEA	Three Phase Transformer	0.1	50	10	0.4	4	1.7	1.7	2.129866	0.03620773	0.017	Y	YN	0	6	Yyn6	4	1.7	2.129866	0.03620773	0.017
0.1 MVA 10/0.4 kV Yyn6 wnr ASEA	Three Phase Transformer	0.1	50	10	0.4	4	1.7	1.7	2.129866	0.03620773	0.017	Y	YN	0	6	Yyn6	4	1.7	2.129866	0.03620773	0.017
0.125 MVA 10/0.4 kV 0.31 GEAFOL	Three Phase Transformer	0.125	50	10	0.4	6	2	1.6	3.614208	0.05782733	0.016	D	YN	0	5	Dyn5	6	1.6	3.614208	0.05782733	0.016
0.125 MVA 10/0.4 kV 0.4 GEAFOL	Three Phase Transformer	0.125	50	10	0.4	6	2	1.6	3.614208	0.05782733	0.016	D	YN	0	5	Dyn5	6	1.6	3.614208	0.05782733	0.016
0.125 MVA 10/0.4 kV 0.41 GEAFOL	Three Phase Transformer	0.125	50	10	0.4	4	2	1.6	2.291288	0.0366606	0.016	D	YN	0	5	Dyn5	4	1.6	2.291288	0.0366606	0.016
0.125 MVA 10/0.4 kV 0.52 GEAFOL	Three Phase Transformer	0.125	50	10	0.4	4	1.9	1.52	2.434175	0.03699946	0.0152	D	YN	0	5	Dyn5	4	1.52	2.434175	0.03699946	0.0152
0.125 MVA 10/0.4 kV DOTE 125/10 SGB	Three Phase Transformer	0.125	50	10	0.4	4	2.05	1.64	2.224599	0.03648342	0.0164	Y	ZN	0	5	Yzn5	4	1.64	2.224599	0.03648342	0.0164
0.125 MVA 10/0.4 kV DOTEL 125/10 SGB	Three Phase Transformer	0.125	50	10	0.4	4	2.05	1.64	2.224599	0.03648342	0.0164	Y	ZN	0	5	Yzn5	4	1.64	2.224599	0.03648342	0.0164
0.125 MVA 10/0.4 kV DOTN 125/10 SGB	Three Phase Transformer	0.125	50	10	0.4	4	2.65	2.12	1.599995	0.0339199	0.0212	Y	ZN	0	5	Yzn5	4	2.12	1.599995	0.0339199	0.0212
0.125 MVA 10/0.4 kV DOTNL 125/10 SGB	Three Phase Transformer	0.125	50	10	0.4	4	2.65	2.12	1.599995	0.0339199	0.0212	Y	ZN	0	5	Yzn5	4	2.12	1.599995	0.0339199	0.0212
0.125 MVA 10/0.4 kV Dyn1 ASEA	Three Phase Transformer	0.125	50	10	0.4	4	2	1.6	2.291288	0.0366606	0.016	D	YN	0	1	Dyn1	4	1.6	2.291288	0.0366606	0.016
0.125 MVA 10/0.4 kV Dyn1 wnr ASEA	Three Phase Transformer	0.125	50	10	0.4	4	2	1.6	2.291288	0.0366606	0.016	D	YN	0	1	Dyn1	4	1.6	2.291288	0.0366606	0.016
0.125 MVA 10/0.4 kV Dyn11 ASEA	Three Phase Transformer	0.125	50	10	0.4	4	2	1.6	2.291288	0.0366606	0.016	D	YN	0	11	Dyn11	4	1.6	2.291288	0.0366606	0.016
0.125 MVA 10/0.4 kV Dyn11 wnr ASEA	Three Phase Transformer	0.125	50	10	0.4	4	2	1.6	2.291288	0.0366606	0.016	D	YN	0	11	Dyn11	4	1.6	2.291288	0.0366606	0.016
0.125 MVA 10/0.4 kV Dyn5 ASEA	Three Phase Transformer	0.125	50	10	0.4	4	2	1.6	2.291288	0.0366606	0.016	D	YN	0	5	Dyn5	4	1.6	2.291288	0.0366606	0.016
0.125 MVA 10/0.4 kV Dyn5 wnr ASEA	Three Phase Transformer	0.125	50	10	0.4	4	2	1.6	2.291288	0.0366606	0.016	D	YN	0	5	Dyn5	4	1.6	2.291288	0.0366606	0.016
0.125 MVA 10/0.4 kV Dyn7 ASEA	Three Phase Transformer	0.125	50	10	0.4	4	2	1.6	2.291288	0.0366606	0.016	D	YN	0	7	Dyn7	4	1.6	2.291288	0.0366606	0.016
0.125 MVA 10/0.4 kV Dyn7 wnr ASEA	Three Phase Transformer	0.125	50	10	0.4	4	2	1.6	2.291288	0.0366606	0.016	D	YN	0	7	Dyn7	4	1.6	2.291288	0.0366606	0.016
0.125 MVA 10/0.4 kV Trafo Union	Three Phase Transformer	0.125	50	10	0.4	4	1.9	1.52	2.434175	0.03699946	0.0152	Y	ZN	0	5	Yzn5	4	1.52	2.434175	0.03699946	0.0152
0.125 MVA 10/0.4 kV Trafo Union wnr	Three Phase Transformer	0.125	50	10	0.4	4	2	1.6	2.291288	0.0366606	0.016	Y	ZN	0	5	Yzn5	4	1.6	2.291288	0.0366606	0.016
0.125 MVA 10/0.4 kV Yyn0 ASEA	Three Phase Transformer	0.125	50	10	0.4	4	2	1.6	2.291288	0.0366606	0.016	Y	YN	0	0	Yyn0	4	1.6	2.291288	0.0366606	0.016
0.125 MVA 10/0.4 kV Yyn0 wnr ASEA	Three Phase Transformer	0.125	50	10	0.4	4	2	1.6	2.291288	0.0366606	0.016	Y	YN	0	0	Yyn0	4	1.6	2.291288	0.0366606	0.016
0.125 MVA 10/0.4 kV Yyn6 ASEA	Three Phase Transformer	0.125	50	10	0.4	4	2	1.6	2.291288	0.0366606	0.016	Y	YN	0	6	Yyn6	4	1.6	2.291288	0.0366606	0.016
0.125 MVA 10/0.4 kV Yyn6 wnr ASEA	Three Phase Transformer	0.125	50	10	0.4	4	2	1.6	2.291288	0.0366606	0.016	Y	YN	0	6	Yyn6	4	1.6	2.291288	0.0366606	0.016
0.16 MVA 10/0.4 kV 0.37 GEAFOL	Three Phase Transformer	0.16	50	10	0.4	6	2.4	1.5	3.872983	0.05809475	0.015	D	YN	0	5	Dyn5	6	1.5	3.872983	0.05809475	0.015
0.16 MVA 10/0.4 kV 0.61 GEAFOL	Three Phase Transformer	0.16	50	10	0.4	4	2.3	1.4375	2.596712	0.03732773	0.014375	D	YN	0	5	Dyn5	4	1.4375	2.596712	0.03732773	0.014375
0.16 MVA 10/0.4 kV 4 GEAFOL	Three Phase Transformer	0.16	50	10	0.4	4	2.3	1.4375	2.596712	0.03732773	0.014375	D	YN	0	5	Dyn5	4	1.4375	2.596712	0.03732773	0.014375
0.16 MVA 10/0.4 kV 6 GEAFOL	Three Phase Transformer	0.16	50	10	0.4	6	2.4	1.5	3.872983	0.05809475	0.015	D	YN	0	5	Dyn5	6	1.5	3.872983	0.05809475	0.015
0.16 MVA 10/0.4 kV DOTE 160/10 SGB	Three Phase Transformer	0.16	50	10	0.4	4	2.35	1.46875	2.533166	0.03720587	0.0146875	Y	ZN	0	5	Yzn5	4	1.46875	2.533166	0.03720587	0.0146875
0.16 MVA 10/0.4 kV DOTEL 160/10 SGB	Three Phase Transformer	0.16	50	10	0.4	4	2.35	1.46875	2.533166	0.03720587	0.0146875	Y	ZN	0	5	Yzn5	4	1.46875	2.533166	0.03720587	0.0146875
0.16 MVA 10/0.4 kV DOTN 160/10 SGB	Three Phase Transformer	0.16	50	10	0.4	4	3.1	1.9375	1.806164	0.03499442	0.019375	Y	ZN	0	5	Yzn5	4	1.9375	1.806164	0.03499442	0.019375
0.16 MVA 10/0.4 kV DOTNL 160/10 SGB	Three Phase Transformer	0.16	50	10	0.4	4	3.1	1.9375	1.806164	0.03499442	0.019375	Y	ZN	0	5	Yzn5	4	1.9375	1.806164	0.03499442	0.019375
0.16 MVA 10/0.4 kV DT 160 SGB	Three Phase Transformer	0.16	50	10	0.4	4	2.3	1.4375	2.596712	0.03732773	0.014375	Y	ZN	0	5	Yzn5	4	1.4375	2.596712	0.03732773	0.014375
0.16 MVA 10/0.4 kV DT 160/10 F SGB	Three Phase Transformer	0.16	50	10	0.4	4	2.3	1.4375	2.596712	0.03732773	0.014375	Y	ZN	0	5	Yzn5	4	1.4375	2.596712	0.03732773	0.014375
0.16 MVA 10/0.4 kV DTKa 3.8 SGB	Three Phase Transformer	0.16	50	10	0.4	3.8	2.4	1.5	2.327612	0.03491418	0.015	Y	ZN	0	5	Yzn5	3.8	1.5	2.327612	0.03491418	0.015
0.16 MVA 10/0.4 kV DTKa 4 SGB	Three Phase Transformer	0.16	50	10	0.4	4	2.6	1.625	2.24926	0.03655048	0.01625	Y	ZN	0	5	Yzn5	4	1.625	2.24926	0.03655048	0.01625
0.16 MVA 10/0.4 kV DTTHL SGB	Three Phase Transformer	0.16	50	10	0.4	4	2.6	1.625	2.24926	0.03655048	0.01625	D	YN	0	5	Dyn5	4	1.625	2.24926	0.03655048	0.01625
0.16 MVA 10/0.4 kV Dyn1 ASEA	Three Phase Transformer	0.16	50	10	0.4	4	2.3	1.4375	2.596712	0.03732773	0.014375	D	YN	0	1	Dyn1	4	1.4375	2.596712	0.03732773	0.014375
0.16 MVA 10/0.4 kV Dyn1 wnr ASEA	Three Phase Transformer	0.16	50	10	0.4	4	2.3	1.4375	2.596712	0.03732773	0.014375	D	YN	0	1	Dyn1	4	1.4375	2.596712	0.03732773	0.014375
0.16 MVA 10/0.4 kV Dyn11 ASEA	Three Phase Transformer	0.16	50	10	0.4	4	2.3	1.4375	2.596712	0.03732773	0.014375	D	YN	0	11	Dyn11	4	1.4375	2.596712	0.03732773	0.014375
0.16 MVA 10/0.4 kV Dyn11 wnr ASEA	Three Phase Transformer	0.16	50	10	0.4	4	2.3	1.4375	2.596712	0.03732773	0.014375	D	YN	0	11	Dyn11	4	1.4375	2.596712	0.03732773	0.014375
0.16 MVA 10/0.4 kV Dyn5 ASEA	Three Phase Transformer	0.16	50	10	0.4	4	2.3	1.4375	2.596712	0.03732773	0.014375	D	YN	0	5	Dyn5	4	1.4375	2.596712	0.03732773	0.014375
0.16 MVA 10/0.4 kV Dyn5 wnr ASEA	Three Phase Transformer	0.16	50	10	0.4	4	2.3	1.4375	2.596712	0.03732773	0.014375	D	YN	0	5	Dyn5	4	1.4375	2.596712	0.03732773	0.014375
0.16 MVA 10/0.4 kV Dyn7 ASEA	Three Phase Transformer	0.16	50	10	0.4	4	2.3	1.4375	2.596712	0.03732773	0.014375	D	YN	0	7	Dyn7	4	1.4375	2.596712	0.03732773	0.014375
0.16 MVA 10/0.4 kV Dyn7 wnr ASEA	Three Phase Transformer	0.16	50	10	0.4	4	2.3	1.4375	2.596712	0.03732773	0.014375	D	YN	0	7	Dyn7	4	1.4375	2.596712	0.03732773	0.014375
0.16 MVA 10/0.4 kV ET 160 SGB	Three Phase Transformer	0.16	50	10	0.4	3.75	2.1	1.3125	2.676428	0.03512812	0.013125	Y	ZN	0	5	Yzn5	3.75	1.3125	2.676428	0.03512812	0.013125
0.16 MVA 10/0.4 kV ET 160/23 SGB	Three Phase Transformer	0.16	50	10	0.4	3.75	2.1	1.3125	2.676428	0.03512812	0.013125	Y	ZN	0	5	Yzn5	3.75	1.3125	2.676428	0.03512812	0.013125
0.16 MVA 10/0.4 kV Trafo Union	Three Phase Transformer	0.16	50	10	0.4	4	2.4	1.5	2.472066	0.03708099	0.015	D	YN	0	5	Dyn5	4	1.5	2.472066	0.03708099	0.015
0.16 MVA 10/0.4 kV Trafo Union wnr	Three Phase Transformer	0.16	50	10	0.4	4	2.5	1.5625	2.356608	0.03682199	0.015625	D	YN	0	5	Dyn5	4	1.5625	2.356608	0.03682199	0.015625
0.16 MVA 10/0.4 kV Yyn0 ASEA	Three Phase Transformer	0.16	50	10	0.4	4	2.3	1.4375	2.596712	0.03732773	0.014375	Y	YN	0	0	Yyn0	4	1.4375	2.596712	0.03732773	0.014375
0.16 MVA 10/0.4 kV Yyn0 wnr ASEA	Three Phase Transformer	0.16	50	10	0.4	4	2.3	1.4375	2.596712	0.03732773	0.014375	Y	YN	0	0	Yyn0	4	1.4375	2.596712	0.03732773	0.014375
0.16 MVA 10/0.4 kV Yyn6 ASEA	Three Phase Transformer	0.16	50	10	0.4	4	2.3	1.4375	2.596712	0.03732773	0.014375	Y	YN	0	6	Yyn6	4	1.4375	2.596712	0.03732773	0.014375
0.16 MVA 10/0.4 kV Yyn6 wnr ASEA	Three Phase Transformer	0.16	50	10	0.4	4	2.3	1.4375	2.596712	0.03732773	0.014375	Y	YN	0	6	Yyn6	4	1.4375	2.596712	0.03732773	0.014375
0.2 MVA 10/0.4 kV 0.44 GEAFOL	Three Phase Transformer	0.2	50	10	0.4	6	2.9	1.45	4.01528	0.05822156	0.0145	D	YN	0	5	Dyn5	6	1.45	4.01528	0.05822156	0.0145
0.2 MVA 10/0.4 kV 0.54 GEAFOL	Three Phase Transformer	0.2	50	10	0.4	4	2.6	1.3	2.909889	0.03782856	0.013	D	YN	0	5	Dyn5	4	1.3	2.909889	0.03782856	0.013
0.2 MVA 10/0.4 kV 0.57 GEAFOL	Three Phase Transformer	0.2	50	10	0.4	6	2.8	1.4	4.167415	0.05834381	0.014	D	YN	0	5	Dyn5	6	1.4	4.167415	0.05834381	0.014
0.2 MVA 10/0.4 kV 0.69 GEAFOL	Three Phase Transformer	0.2	50	10	0.4	4	2.65	1.325	2.848432	0.03774172	0.01325	D	YN	0	5	Dyn5	4	1.325	2.848432	0.03774172	0.01325
0.2 MVA 10/0.4 kV DOTE 200/10 SGB	Three Phase Transformer	0.2	50	10	0.4	4	2.85	1.425	2.622851	0.03737563	0.01425	Y	ZN	0	5	Yzn5	4	1.425	2.622851	0.03737563	0.01425
0.2 MVA 10/0.4 kV DOTEL 200/10 SGB	Three Phase Transformer	0.2	50	10	0.4	4	2.85	1.425	2.622851	0.03737563	0.01425	Y	ZN	0	5	Yzn5	4	1.425	2.622851	0.03737563	0.01425
0.2 MVA 10/0.4 kV DOTN 200/10 SGB	Three Phase Transformer	0.2	50	10	0.4	4	3.6	1.8	1.984508	0.03572114	0.018	Y	ZN	0	5	Yzn5	4	1.8	1.984508	0.03572114	0.018
0.2 MVA 10/0.4 kV DOTNL 200/10 SGB	Three Phase Transformer	0.2	50	10	0.4	4	3.6	1.8	1.984508	0.03572114	0.018	Y	ZN	0	5	Yzn5	4	1.8	1.984508	0.03572114	0.018
0.2 MVA 10/0.4 kV DT 200 SGB	Three Phase Transformer	0.2	50	10	0.4	4	2.8	1.4	2.676428	0.03746999	0.014	Y	ZN	0	5	Yzn5	4	1.4	2.676428	0.03746999	0.014
0.2 MVA 10/0.4 kV DT 200/10 F SGB	Three Phase Transformer	0.2	50	10	0.4	4	2.3	1.15	3.331411	0.03831122	0.0115	Y	ZN	0	5	Yzn5	4	1.15	3.331411	0.03831122	0.0115
0.2 MVA 10/0.4 kV Dyn1 ASEA	Three Phase Transformer	0.2	50	10	0.4	4	2.75	1.375	2.731814	0.03756245	0.01375	D	YN	0	1	Dyn1	4	1.375	2.731814	0.03756245	0.01375
0.2 MVA 10/0.4 kV Dyn1 wnr ASEA	Three Phase Transformer	0.2	50	10	0.4	4	2.75	1.375	2.731814	0.03756245	0.01375	D	YN	0	1	Dyn1	4	1.375	2.731814	0.03756245	0.01375
0.2 MVA 10/0.4 kV Dyn11 ASEA	Three Phase Transformer	0.2	50	10	0.4	4	2.75	1.375	2.731814	0.03756245	0.01375	D	YN	0	11	Dyn11	4	1.375	2.731814	0.03756245	0.01375
0.2 MVA 10/0.4 kV Dyn11 wnr ASEA	Three Phase Transformer	0.2	50	10	0.4	4	2.75	1.375	2.731814	0.03756245	0.01375	D	YN	0	11	Dyn11	4	1.375	2.731814	0.03756245	0.01375
0.2 MVA 10/0.4 kV Dyn5 ASEA	Three Phase Transformer	0.2	50	10	0.4	4	2.75	1.375	2.731814	0.03756245	0.01375	D	YN	0	5	Dyn5	4	1.375	2.731814	0.03756245	0.01375
0.2 MVA 10/0.4 kV Dyn5 wnr ASEA	Three Phase Transformer	0.2	50	10	0.4	4	2.75	1.375	2.731814	0.03756245	0.01375	D	YN	0	5	Dyn5	4	1.375	2.731814	0.03756245	0.01375
0.2 MVA 10/0.4 kV Dyn7 ASEA	Three Phase Transformer	0.2	50	10	0.4	4	2.75	1.375	2.731814	0.03756245	0.01375	D	YN	0	7	Dyn7	4	1.375	2.731814	0.03756245	0.01375
0.2 MVA 10/0.4 kV Dyn7 wnr ASEA	Three Phase Transformer	0.2	50	10	0.4	4	2.75	1.375	2.731814	0.03756245	0.01375	D	YN	0	7	Dyn7	4	1.375	2.731814	0.03756245	0.01375
0.2 MVA 10/0.4 kV Trafo Union	Three Phase Transformer	0.2	50	10	0.4	4	2.5	1.25	3.039737	0.03799671	0.0125	D	YN	0	5	Dyn5	4	1.25	3.039737	0.03799671	0.0125
0.2 MVA 10/0.4 kV Trafo Union wnr	Three Phase Transformer	0.2	50	10	0.4	4	2.5	1.25	3.039737	0.03799671	0.0125	D	YN	0	5	Dyn5	4	1.25	3.039737	0.03799671	0.0125
0.2 MVA 10/0.4 kV Yyn0 ASEA	Three Phase Transformer	0.2	50	10	0.4	4	2.75	1.375	2.731814	0.03756245	0.01375	Y	YN	0	0	Yyn0	4	1.375	2.731814	0.03756245	0.01375
0.2 MVA 10/0.4 kV Yyn0 wnr ASEA	Three Phase Transformer	0.2	50	10	0.4	4	2.75	1.375	2.731814	0.03756245	0.01375	Y	YN	0	0	Yyn0	4	1.375	2.731814	0.03756245	0.01375
0.2 MVA 10/0.4 kV Yyn6 ASEA	Three Phase Transformer	0.2	50	10	0.4	4	2.75	1.375	2.731814	0.03756245	0.01375	Y	YN	0	6	Yyn6	4	1.375	2.731814	0.03756245	0.01375
0.2 MVA 10/0.4 kV Yyn6 wnr ASEA	Three Phase Transformer	0.2	50	10	0.4	4	2.75	1.375	2.731814	0.03756245	0.01375	Y	YN	0	6	Yyn6	4	1.375	2.731814	0.03756245	0.01375
0.25 MVA 10/0.4 kV 0.4 Trafo Union wnr	Three Phase Transformer	0.25	50	10	0.4	4	3	1.2	3.179797	0.03815757	0.012	D	YN	0	5	Dyn5	4	1.2	3.179797	0.03815757	0.012
0.25 MVA 10/0.4 kV 0.5 Trafo Union	Three Phase Transformer	0.25	50	10	0.4	4	2.9	1.16	3.300092	0.03828106	0.0116	D	YN	0	5	Dyn5	4	1.16	3.300092	0.03828106	0.0116
0.25 MVA 10/0.4 kV 0.54 GEAFOL	Three Phase Transformer	0.25	50	10	0.4	6	3.4	1.36	4.296937	0.05843834	0.0136	D	YN	0	5	Dyn5	6	1.36	4.296937	0.05843834	0.0136
0.25 MVA 10/0.4 kV 0.6 Trafo Union wnr	Three Phase Transformer	0.25	50	10	0.4	4	3	1.2	3.179797	0.03815757	0.012	D	YN	0	5	Dyn5	4	1.2	3.179797	0.03815757	0.012
0.25 MVA 10/0.4 kV 0.64 GEAFOL	Three Phase Transformer	0.25	50	10	0.4	4	3	1.2	3.179797	0.03815757	0.012	D	YN	0	5	Dyn5	4	1.2	3.179797	0.03815757	0.012
0.25 MVA 10/0.4 kV 0.69 GEAFOL	Three Phase Transformer	0.25	50	10	0.4	6	3	1.2	4.898979	0.05878775	0.012	D	YN	0	5	Dyn5	6	1.2	4.898979	0.05878775	0.012
0.25 MVA 10/0.4 kV 0.77 Trafo Union	Three Phase Transformer	0.25	50	10	0.4	4	2.9	1.16	3.300092	0.03828106	0.0116	D	YN	0	5	Dyn5	4	1.16	3.300092	0.03828106	0.0116
0.25 MVA 10/0.4 kV 0.82 GEAFOL	Three Phase Transformer	0.25	50	10	0.4	4	3	1.2	3.179797	0.03815757	0.012	D	YN	0	5	Dyn5	4	1.2	3.179797	0.03815757	0.012
0.25 MVA 10/0.4 kV DOTE 250/10 SGB	Three Phase Transformer	0.25	50	10	0.4	4	3.25	1.3	2.909889	0.03782856	0.013	Y	ZN	0	5	Yzn5	4	1.3	2.909889	0.03782856	0.013
0.25 MVA 10/0.4 kV DOTEL 250/10 SGB	Three Phase Transformer	0.25	50	10	0.4	4	3.25	1.3	2.909889	0.03782856	0.013	Y	ZN	0	5	Yzn5	4	1.3	2.909889	0.03782856	0.013
0.25 MVA 10/0.4 kV DOTN 250/10 SGB	Three Phase Transformer	0.25	50	10	0.4	4	4.1	1.64	2.224599	0.03648342	0.0164	Y	ZN	0	5	Yzn5	4	1.64	2.224599	0.03648342	0.0164
0.25 MVA 10/0.4 kV DOTNL 250/10 SGB	Three Phase Transformer	0.25	50	10	0.4	4	4.1	1.64	2.224599	0.03648342	0.0164	Y	ZN	0	5	Yzn5	4	1.64	2.224599	0.03648342	0.0164
0.25 MVA 10/0.4 kV DT 250 SGB	Three Phase Transformer	0.25	50	10	0.4	4	3.2	1.28	2.96068	0.0378967	0.0128	Y	ZN	0	5	Yzn5	4	1.28	2.96068	0.0378967	0.0128
0.25 MVA 10/0.4 kV DT 250/10 F SGB	Three Phase Transformer	0.25	50	10	0.4	6	3.4	1.36	4.296937	0.05843834	0.0136	Y	ZN	0	5	Yzn5	6	1.36	4.296937	0.05843834	0.0136
0.25 MVA 10/0.4 kV DTKa SGB	Three Phase Transformer	0.25	50	10	0.4	6	3.2	1.28	4.579591	0.05861877	0.0128	Y	ZN	0	5	Yzn5	6	1.28	4.579591	0.05861877	0.0128
0.25 MVA 10/0.4 kV DTTHL SGB	Three Phase Transformer	0.25	50	10	0.4	4	3	1.2	3.179797	0.03815757	0.012	D	YN	0	5	Dyn5	4	1.2	3.179797	0.03815757	0.012
0.25 MVA 10/0.4 kV Dyn1 4 ASEA	Three Phase Transformer	0.25	50	10	0.4	4	3	1.2	3.179797	0.03815757	0.012	D	YN	0	1	Dyn1	4	1.2	3.179797	0.03815757	0.012
0.25 MVA 10/0.4 kV Dyn1 4 wnr ASEA	Three Phase Transformer	0.25	50	10	0.4	4	3	1.2	3.179797	0.03815757	0.012	D	YN	0	1	Dyn1	4	1.2	3.179797	0.03815757	0.012
0.25 MVA 10/0.4 kV Dyn1 6 ASEA	Three Phase Transformer	0.25	50	10	0.4	6	3.4	1.36	4.296937	0.05843834	0.0136	D	YN	0	1	Dyn1	6	1.36	4.296937	0.05843834	0.0136
0.25 MVA 10/0.4 kV Dyn1 6 wnr ASEA	Three Phase Transformer	0.25	50	10	0.4	6	3.4	1.36	4.296937	0.05843834	0.0136	D	YN	0	1	Dyn1	6	1.36	4.296937	0.05843834	0.0136
0.25 MVA 10/0.4 kV Dyn11 4 ASEA	Three Phase Transformer	0.25	50	10	0.4	4	3	1.2	3.179797	0.03815757	0.012	D	YN	0	11	Dyn11	4	1.2	3.179797	0.03815757	0.012
0.25 MVA 10/0.4 kV Dyn11 4 wnr ASEA	Three Phase Transformer	0.25	50	10	0.4	4	3	1.2	3.179797	0.03815757	0.012	D	YN	0	11	Dyn11	4	1.2	3.179797	0.03815757	0.012
0.25 MVA 10/0.4 kV Dyn11 6 ASEA	Three Phase Transformer	0.25	50	10	0.4	6	3.4	1.36	4.296937	0.05843834	0.0136	D	YN	0	11	Dyn11	6	1.36	4.296937	0.05843834	0.0136
0.25 MVA 10/0.4 kV Dyn11 6 wnr ASEA	Three Phase Transformer	0.25	50	10	0.4	6	3.4	1.36	4.296937	0.05843834	0.0136	D	YN	0	11	Dyn11	6	1.36	4.296937	0.05843834	0.0136
0.25 MVA 10/0.4 kV Dyn5 4 ASEA	Three Phase Transformer	0.25	50	10	0.4	4	3	1.2	3.179797	0.03815757	0.012	D	YN	0	5	Dyn5	4	1.2	3.179797	0.03815757	0.012
0.25 MVA 10/0.4 kV Dyn5 4 wnr ASEA	Three Phase Transformer	0.25	50	10	0.4	4	3	1.2	3.179797	0.03815757	0.012	D	YN	0	5	Dyn5	4	1.2	3.179797	0.03815757	0.012
0.25 MVA 10/0.4 kV Dyn5 6 ASEA	Three Phase Transformer	0.25	50	10	0.4	6	3.4	1.36	4.296937	0.05843834	0.0136	D	YN	0	5	Dyn5	6	1.36	4.296937	0.05843834	0.0136
0.25 MVA 10/0.4 kV Dyn5 6 wnr ASEA	Three Phase Transformer	0.25	50	10	0.4	6	3.4	1.36	4.296937	0.05843834	0.0136	D	YN	0	5	Dyn5	6	1.36	4.296937	0.05843834	0.0136
0.25 MVA 10/0.4 kV Dyn7 4 ASEA	Three Phase Transformer	0.25	50	10	0.4	4	3	1.2	3.179797	0.03815757	0.012	D	YN	0	7	Dyn7	4	1.2	3.179797	0.03815757	0.012
0.25 MVA 10/0.4 kV Dyn7 4 wnr ASEA	Three Phase Transformer	0.25	50	10	0.4	4	3	1.2	3.179797	0.03815757	0.012	D	YN	0	7	Dyn7	4	1.2	3.179797	0.03815757	0.012
0.25 MVA 10/0.4 kV Dyn7 6 ASEA	Three Phase Transformer	0.25	50	10	0.4	6	3.4	1.36	4.296937	0.05843834	0.0136	D	YN	0	7	Dyn7	6	1.36	4.296937	0.05843834	0.0136
0.25 MVA 10/0.4 kV Dyn7 6 wnr ASEA	Three Phase Transformer	0.25	50	10	0.4	6	3.4	1.36	4.296937	0.05843834	0.0136	D	YN	0	7	Dyn7	6	1.36	4.296937	0.05843834	0.0136
0.25 MVA 10/0.4 kV ET 250 SGB	Three Phase Transformer	0.25	50	10	0.4	3.75	3	1.2	2.96068	0.03552816	0.012	Y	ZN	0	5	Yzn5	3.75	1.2	2.96068	0.03552816	0.012
0.25 MVA 10/0.4 kV ET 250/23 SGB	Three Phase Transformer	0.25	50	10	0.4	3.75	3	1.2	2.96068	0.03552816	0.012	Y	ZN	0	5	Yzn5	3.75	1.2	2.96068	0.03552816	0.012
0.25 MVA 10/0.4 kV Yyn0 4 ASEA	Three Phase Transformer	0.25	50	10	0.4	4	3	1.2	3.179797	0.03815757	0.012	Y	YN	0	0	Yyn0	4	1.2	3.179797	0.03815757	0.012
0.25 MVA 10/0.4 kV Yyn0 4 wnr ASEA	Three Phase Transformer	0.25	50	10	0.4	4	3	1.2	3.179797	0.03815757	0.012	Y	YN	0	0	Yyn0	4	1.2	3.179797	0.03815757	0.012
0.25 MVA 10/0.4 kV Yyn0 6 ASEA	Three Phase Transformer	0.25	50	10	0.4	6	3.4	1.36	4.296937	0.05843834	0.0136	Y	YN	0	0	Yyn0	6	1.36	4.296937	0.05843834	0.0136
0.25 MVA 10/0.4 kV Yyn0 6wnr ASEA	Three Phase Transformer	0.25	50	10	0.4	6	3.4	1.36	4.296937	0.05843834	0.0136	Y	YN	0	0	Yyn0	6	1.36	4.296937	0.05843834	0.0136
0.25 MVA 10/0.4 kV Yyn6 4 ASEA	Three Phase Transformer	0.25	50	10	0.4	4	3	1.2	3.179797	0.03815757	0.012	Y	YN	0	6	Yyn6	4	1.2	3.179797	0.03815757	0.012
0.25 MVA 10/0.4 kV Yyn6 4 wnr ASEA	Three Phase Transformer	0.25	50	10	0.4	4	3	1.2	3.179797	0.03815757	0.012	Y	YN	0	6	Yyn6	4	1.2	3.179797	0.03815757	0.012
0.25 MVA 10/0.4 kV Yyn6 6 ASEA	Three Phase Transformer	0.25	50	10	0.4	6	3.4	1.36	4.296937	0.05843834	0.0136	Y	YN	0	6	Yyn6	6	1.36	4.296937	0.05843834	0.0136
0.25 MVA 10/0.4 kV Yyn6 6 wnr ASEA	Three Phase Transformer	0.25	50	10	0.4	6	3.4	1.36	4.296937	0.05843834	0.0136	Y	YN	0	6	Yyn6	6	1.36	4.296937	0.05843834	0.0136
0.315 MVA 0.4/10kV DOTEL 315/10 SGB	Three Phase Transformer	0.315	50	10	0.4	4	3.9	1.238095	3.072112	0.03803567	0.01238095	Y	ZN	0	5	Yzn5	4	1.238095	3.072112	0.03803567	0.01238095
0.315 MVA 10/0.4 kV 0.64 GEAFOL	Three Phase Transformer	0.315	50	10	0.4	6	3.8	1.206349	4.872118	0.05877475	0.01206349	D	YN	0	5	Dyn5	6	1.206349	4.872118	0.05877475	0.01206349
0.315 MVA 10/0.4 kV 0.74 GEAFOL	Three Phase Transformer	0.315	50	10	0.4	4	3.6	1.142857	3.354102	0.03833259	0.01142857	D	YN	0	5	Dyn5	4	1.142857	3.354102	0.03833259	0.01142857
0.315 MVA 10/0.4 kV 0.82 GEAFOL	Three Phase Transformer	0.315	50	10	0.4	6	3.4	1.079365	5.468136	0.05902116	0.01079365	D	YN	0	5	Dyn5	6	1.079365	5.468137	0.05902116	0.01079365
0.315 MVA 10/0.4 kV 0.95 GEAFOL	Three Phase Transformer	0.315	50	10	0.4	4	3.5	1.111111	3.458323	0.03842581	0.01111111	D	YN	0	5	Dyn5	4	1.111111	3.458323	0.03842581	0.01111111
0.315 MVA 10/0.4 kV DOTE 315/10 SGB	Three Phase Transformer	0.315	50	10	0.4	4	3.9	1.238095	3.072112	0.03803567	0.01238095	Y	ZN	0	5	Yzn5	4	1.238095	3.072112	0.03803567	0.01238095
0.315 MVA 10/0.4 kV DOTN 315/10 SGB	Three Phase Transformer	0.315	50	10	0.4	4	4.9	1.555556	2.369018	0.03685139	0.01555556	Y	ZN	0	5	Yzn5	4	1.555556	2.369017	0.03685138	0.01555556
0.315 MVA 10/0.4 kV DOTNL 315/10 SGB	Three Phase Transformer	0.315	50	10	0.4	4	4.9	1.555556	2.369018	0.03685139	0.01555556	Y	ZN	0	5	Yzn5	4	1.555556	2.369017	0.03685138	0.01555556
0.315 MVA 10/0.4 kV DT 315 SGB	Three Phase Transformer	0.315	50	10	0.4	4	4	1.269841	2.987055	0.03793086	0.01269841	Y	ZN	0	5	Yzn5	4	1.269841	2.987056	0.03793086	0.01269841
0.315 MVA 10/0.4 kV DT 315/10 F SGB	Three Phase Transformer	0.315	50	10	0.4	6	4	1.269841	4.617968	0.05864086	0.01269841	Y	ZN	0	5	Yzn5	6	1.269841	4.617969	0.05864086	0.01269841
0.315 MVA 10/0.4 kV Dyn1 4 ASEA	Three Phase Transformer	0.315	50	10	0.4	4	3.65	1.15873	3.30404	0.03828491	0.0115873	D	YN	0	1	Dyn1	4	1.15873	3.304041	0.03828491	0.0115873
0.315 MVA 10/0.4 kV Dyn1 4 wnr ASEA	Three Phase Transformer	0.315	50	10	0.4	4	3.65	1.15873	3.30404	0.03828491	0.0115873	D	YN	0	1	Dyn1	4	1.15873	3.304041	0.03828491	0.0115873
0.315 MVA 10/0.4 kV Dyn1 6 ASEA	Three Phase Transformer	0.315	50	10	0.4	6	4.1	1.301587	4.499983	0.05857121	0.01301587	D	YN	0	1	Dyn1	6	1.301587	4.499984	0.05857121	0.01301587
0.315 MVA 10/0.4 kV Dyn1 6 wnr ASEA	Three Phase Transformer	0.315	50	10	0.4	6	4.1	1.301587	4.499983	0.05857121	0.01301587	D	YN	0	1	Dyn1	6	1.301587	4.499984	0.05857121	0.01301587
0.315 MVA 10/0.4 kV Dyn11 4 ASEA	Three Phase Transformer	0.315	50	10	0.4	4	3.65	1.15873	3.30404	0.03828491	0.0115873	D	YN	0	11	Dyn11	4	1.15873	3.304041	0.03828491	0.0115873
0.315 MVA 10/0.4 kV Dyn11 4wnr ASEA	Three Phase Transformer	0.315	50	10	0.4	4	3.65	1.15873	3.30404	0.03828491	0.0115873	D	YN	0	11	Dyn11	4	1.15873	3.304041	0.03828491	0.0115873
0.315 MVA 10/0.4 kV Dyn11 6 ASEA	Three Phase Transformer	0.315	50	10	0.4	6	4.1	1.301587	4.499983	0.05857121	0.01301587	D	YN	0	11	Dyn11	6	1.301587	4.499984	0.05857121	0.01301587
0.315 MVA 10/0.4 kV Dyn11 6wnr ASEA	Three Phase Transformer	0.315	50	10	0.4	6	4.1	1.301587	4.499983	0.05857121	0.01301587	D	YN	0	11	Dyn11	6	1.301587	4.499984	0.05857121	0.01301587
0.315 MVA 10/0.4 kV Dyn5 4 ASEA	Three Phase Transformer	0.315	50	10	0.4	4	3.65	1.15873	3.30404	0.03828491	0.0115873	D	YN	0	5	Dyn5	4	1.15873	3.304041	0.03828491	0.0115873
0.315 MVA 10/0.4 kV Dyn5 4 wnr ASEA	Three Phase Transformer	0.315	50	10	0.4	4	3.65	1.15873	3.30404	0.03828491	0.0115873	D	YN	0	5	Dyn5	4	1.15873	3.304041	0.03828491	0.0115873
0.315 MVA 10/0.4 kV Dyn5 6 ASEA	Three Phase Transformer	0.315	50	10	0.4	6	4.1	1.301587	4.499983	0.05857121	0.01301587	D	YN	0	5	Dyn5	6	1.301587	4.499984	0.05857121	0.01301587
0.315 MVA 10/0.4 kV Dyn5 6 wnr ASEA	Three Phase Transformer	0.315	50	10	0.4	6	4.1	1.301587	4.499983	0.05857121	0.01301587	D	YN	0	5	Dyn5	6	1.301587	4.499984	0.05857121	0.01301587
0.315 MVA 10/0.4 kV Dyn7 4 ASEA	Three Phase Transformer	0.315	50	10	0.4	4	3.65	1.15873	3.30404	0.03828491	0.0115873	D	YN	0	7	Dyn7	4	1.15873	3.304041	0.03828491	0.0115873
0.315 MVA 10/0.4 kV Dyn7 4wnr ASEA	Three Phase Transformer	0.315	50	10	0.4	4	3.65	1.15873	3.30404	0.03828491	0.0115873	D	YN	0	7	Dyn7	4	1.15873	3.304041	0.03828491	0.0115873
0.315 MVA 10/0.4 kV Dyn7 6 ASEA	Three Phase Transformer	0.315	50	10	0.4	6	4.1	1.301587	4.499983	0.05857121	0.01301587	D	YN	0	7	Dyn7	6	1.301587	4.499984	0.05857121	0.01301587
0.315 MVA 10/0.4 kV Dyn7 6wnr ASEA	Three Phase Transformer	0.315	50	10	0.4	6	4.1	1.301587	4.499983	0.05857121	0.01301587	D	YN	0	7	Dyn7	6	1.301587	4.499984	0.05857121	0.01301587
0.315 MVA 10/0.4 kV Trafo Union	Three Phase Transformer	0.315	50	10	0.4	4	4	1.269841	2.987055	0.03793086	0.01269841	D	YN	0	5	Dyn5	4	1.269841	2.987056	0.03793086	0.01269841
0.315 MVA 10/0.4 kV Trafo Union wnr	Three Phase Transformer	0.315	50	10	0.4	4	4.2	1.333333	2.828427	0.03771236	0.01333333	D	YN	0	5	Dyn5	4	1.333333	2.828428	0.03771236	0.01333333
0.315 MVA 10/0.4 kV Yyn0 4 ASEA	Three Phase Transformer	0.315	50	10	0.4	4	3.65	1.15873	3.30404	0.03828491	0.0115873	Y	YN	0	0	Yyn0	4	1.15873	3.304041	0.03828491	0.0115873
0.315 MVA 10/0.4 kV Yyn0 4wnr ASEA	Three Phase Transformer	0.315	50	10	0.4	4	3.65	1.15873	3.30404	0.03828491	0.0115873	Y	YN	0	0	Yyn0	4	1.15873	3.304041	0.03828491	0.0115873
0.315 MVA 10/0.4 kV Yyn0 6 ASEA	Three Phase Transformer	0.315	50	10	0.4	6	4.1	1.301587	4.499983	0.05857121	0.01301587	Y	YN	0	0	Yyn0	6	1.301587	4.499984	0.05857121	0.01301587
0.315 MVA 10/0.4 kV Yyn0 6 wnr ASEA	Three Phase Transformer	0.315	50	10	0.4	6	4.1	1.301587	4.499983	0.05857121	0.01301587	Y	YN	0	0	Yyn0	6	1.301587	4.499984	0.05857121	0.01301587
0.315 MVA 10/0.4 kV Yyn6 4 ASEA	Three Phase Transformer	0.315	50	10	0.4	4	3.65	1.15873	3.30404	0.03828491	0.0115873	Y	YN	0	6	Yyn6	4	1.15873	3.304041	0.03828491	0.0115873
0.315 MVA 10/0.4 kV Yyn6 4 wnr ASEA	Three Phase Transformer	0.315	50	10	0.4	4	3.65	1.15873	3.30404	0.03828491	0.0115873	Y	YN	0	6	Yyn6	4	1.15873	3.304041	0.03828491	0.0115873
0.315 MVA 10/0.4 kV Yyn6 6 ASEA	Three Phase Transformer	0.315	50	10	0.4	6	4.1	1.301587	4.499983	0.05857121	0.01301587	Y	YN	0	6	Yyn6	6	1.301587	4.499984	0.05857121	0.01301587
0.315 MVA 10/0.4 kV Yyn6 6 wnr ASEA	Three Phase Transformer	0.315	50	10	0.4	6	4.1	1.301587	4.499983	0.05857121	0.01301587	Y	YN	0	6	Yyn6	6	1.301587	4.499984	0.05857121	0.01301587
0.4 MVA 10/0.4 kV 0.78 GEAFOL	Three Phase Transformer	0.4	50	10	0.4	6	4.1	1.025	5.76761	0.059118	0.01025	D	YN	0	5	Dyn5	6	1.025	5.76761	0.059118	0.01025
0.4 MVA 10/0.4 kV 0.9 GEAFOL	Three Phase Transformer	0.4	50	10	0.4	4	4.3	1.075	3.584037	0.0385284	0.01075	D	YN	0	5	Dyn5	4	1.075	3.584037	0.0385284	0.01075
0.4 MVA 10/0.4 kV 1 GEAFOL	Three Phase Transformer	0.4	50	10	0.4	6	3.9	0.975	6.072052	0.05920251	0.00975	D	YN	0	5	Dyn5	6	0.975	6.072052	0.05920251	0.00975
0.4 MVA 10/0.4 kV 1 GEAFOL/FC	Three Phase Transformer	0.4	50	10	0.4	6	4.4	1.1	5.362095	0.05898305	0.011	D	YN	0	5	Dyn5	6	1.1	5.362095	0.05898305	0.011
0.4 MVA 10/0.4 kV 1.15 GEAFOL	Three Phase Transformer	0.4	50	10	0.4	4	3.7	0.925	4.20711	0.03891577	0.00925	D	YN	0	5	Dyn5	4	0.925	4.20711	0.03891577	0.00925	Three Phase Transformer	0.4	50	10	0.4	4	4.6	1.15	3.331411	0.03831122	0.0115	Y	ZN	0	5	Yzn5	4	1.15	3.331411	0.03831122	0.0115	2.9997	0	302.7	0	300.3	0	0.029997	9999999	0	3.027	9999999	0	3.003	9999999	0	9999999	9999999	9999999	9999999	9999999
0.4 MVA 10/0.4 kV DOTEL 400/10 SGB	Three Phase Transformer	0.4	50	10	0.4	4	4.6	1.15	3.331411	0.03831122	0.0115	Y	ZN	0	5	Yzn5	4	1.15	3.331411	0.03831122	0.0115
0.4 MVA 10/0.4 kV DOTN 400/10 SGB	Three Phase Transformer	0.4	50	10	0.4	4	6	1.5	2.472066	0.03708099	0.015	Y	ZN	0	5	Yzn5	4	1.5	2.472066	0.03708099	0.015
0.4 MVA 10/0.4 kV DOTNL 400/10 SGB	Three Phase Transformer	0.4	50	10	0.4	4	6	1.5	2.472066	0.03708099	0.015	Y	ZN	0	5	Yzn5	4	1.5	2.472066	0.03708099	0.015
0.4 MVA 10/0.4 kV DT 400 SGB	Three Phase Transformer	0.4	50	10	0.4	4	4.6	1.15	3.331411	0.03831122	0.0115	Y	ZN	0	5	Yzn5	4	1.15	3.331411	0.03831122	0.0115
0.4 MVA 10/0.4 kV DT 400/10 F SGB	Three Phase Transformer	0.4	50	10	0.4	6	4.6	1.15	5.120661	0.0588876	0.0115	Y	ZN	0	5	Yzn5	6	1.15	5.120661	0.0588876	0.0115
0.4 MVA 10/0.4 kV DTKa SGB	Three Phase Transformer	0.4	50	10	0.4	6	4.5	1.125	5.238745	0.05893588	0.01125	Y	ZN	0	5	Yzn5	6	1.125	5.238744	0.05893588	0.01125
0.4 MVA 10/0.4 kV DTTH SGB	Three Phase Transformer	0.4	50	10	0.4	4	4.3	1.075	3.584037	0.0385284	0.01075	D	YN	0	5	Dyn5	4	1.075	3.584037	0.0385284	0.01075
0.4 MVA 10/0.4 kV DTTHL SGB	Three Phase Transformer	0.4	50	10	0.4	4	4.3	1.075	3.584037	0.0385284	0.01075	D	YN	0	5	Dyn5	4	1.075	3.584037	0.0385284	0.01075
0.4 MVA 10/0.4 kV DTTHYL SGB	Three Phase Transformer	0.4	50	10	0.4	6	4.3	1.075	5.491081	0.05902912	0.01075	D	YN	0	5	Dyn5	6	1.075	5.491081	0.05902912	0.01075
0.4 MVA 10/0.4 kV Dyn1 4 ASEA	Three Phase Transformer	0.4	50	10	0.4	4	4.3	1.075	3.584037	0.0385284	0.01075	D	YN	0	1	Dyn1	4	1.075	3.584037	0.0385284	0.01075
0.4 MVA 10/0.4 kV Dyn1 4 wnr ASEA	Three Phase Transformer	0.4	50	10	0.4	4	4.3	1.075	3.584037	0.0385284	0.01075	D	YN	0	1	Dyn1	4	1.075	3.584037	0.0385284	0.01075
0.4 MVA 10/0.4 kV Dyn1 6 ASEA	Three Phase Transformer	0.4	50	10	0.4	6	5	1.25	4.694677	0.05868347	0.0125	D	YN	0	1	Dyn1	6	1.25	4.694677	0.05868347	0.0125
0.4 MVA 10/0.4 kV Dyn1 6 wnr ASEA	Three Phase Transformer	0.4	50	10	0.4	6	5	1.25	4.694677	0.05868347	0.0125	D	YN	0	1	Dyn1	6	1.25	4.694677	0.05868347	0.0125
0.4 MVA 10/0.4 kV Dyn11 4 ASEA	Three Phase Transformer	0.4	50	10	0.4	4	4.3	1.075	3.584037	0.0385284	0.01075	D	YN	0	11	Dyn11	4	1.075	3.584037	0.0385284	0.01075
0.4 MVA 10/0.4 kV Dyn11 4 wnr ASEA	Three Phase Transformer	0.4	50	10	0.4	4	4.3	1.075	3.584037	0.0385284	0.01075	D	YN	0	11	Dyn11	4	1.075	3.584037	0.0385284	0.01075
0.4 MVA 10/0.4 kV Dyn11 6 ASEA	Three Phase Transformer	0.4	50	10	0.4	6	5	1.25	4.694677	0.05868347	0.0125	D	YN	0	11	Dyn11	6	1.25	4.694677	0.05868347	0.0125
0.4 MVA 10/0.4 kV Dyn11 6wnr ASEA	Three Phase Transformer	0.4	50	10	0.4	6	5	1.25	4.694677	0.05868347	0.0125	D	YN	0	11	Dyn11	6	1.25	4.694677	0.05868347	0.0125
0.4 MVA 10/0.4 kV Dyn5 4 ASEA	Three Phase Transformer	0.4	50	10	0.4	4	4.3	1.075	3.584037	0.0385284	0.01075	D	YN	0	5	Dyn5	4	1.075	3.584037	0.0385284	0.01075
0.4 MVA 10/0.4 kV Dyn5 4 wnr ASEA	Three Phase Transformer	0.4	50	10	0.4	4	4.3	1.075	3.584037	0.0385284	0.01075	D	YN	0	5	Dyn5	4	1.075	3.584037	0.0385284	0.01075
0.4 MVA 10/0.4 kV Dyn5 6 ASEA	Three Phase Transformer	0.4	50	10	0.4	6	5	1.25	4.694677	0.05868347	0.0125	D	YN	0	5	Dyn5	6	1.25	4.694677	0.05868347	0.0125
0.4 MVA 10/0.4 kV Dyn5 6 wnr ASEA	Three Phase Transformer	0.4	50	10	0.4	6	5	1.25	4.694677	0.05868347	0.0125	D	YN	0	5	Dyn5	6	1.25	4.694677	0.05868347	0.0125
0.4 MVA 10/0.4 kV Dyn7 4 ASEA	Three Phase Transformer	0.4	50	10	0.4	4	4.3	1.075	3.584037	0.0385284	0.01075	D	YN	0	7	Dyn7	4	1.075	3.584037	0.0385284	0.01075
0.4 MVA 10/0.4 kV Dyn7 4 wnr ASEA	Three Phase Transformer	0.4	50	10	0.4	4	4.3	1.075	3.584037	0.0385284	0.01075	D	YN	0	7	Dyn7	4	1.075	3.584037	0.0385284	0.01075
0.4 MVA 10/0.4 kV Dyn7 6 ASEA	Three Phase Transformer	0.4	50	10	0.4	6	5	1.25	4.694677	0.05868347	0.0125	D	YN	0	7	Dyn7	6	1.25	4.694677	0.05868347	0.0125
0.4 MVA 10/0.4 kV Dyn7 6 wnr ASEA	Three Phase Transformer	0.4	50	10	0.4	6	5	1.25	4.694677	0.05868347	0.0125	D	YN	0	7	Dyn7	6	1.25	4.694677	0.05868347	0.0125
0.4 MVA 10/0.4 kV Trafo Union	Three Phase Transformer	0.4	50	10	0.4	4	5	1.25	3.039737	0.03799671	0.0125	D	YN	0	5	Dyn5	4	1.25	3.039737	0.03799671	0.0125
0.4 MVA 10/0.4 kV Trafo Union wnr	Three Phase Transformer	0.4	50	10	0.4	4	5.3	1.325	2.848432	0.03774172	0.01325	D	YN	0	5	Dyn5	4	1.325	2.848432	0.03774172	0.01325
0.4 MVA 10/0.4 kV Yyn0 4 ASEA	Three Phase Transformer	0.4	50	10	0.4	4	4.3	1.075	3.584037	0.0385284	0.01075	Y	YN	0	0	Yyn0	4	1.075	3.584037	0.0385284	0.01075
0.4 MVA 10/0.4 kV Yyn0 4 wnr ASEA	Three Phase Transformer	0.4	50	10	0.4	4	4.3	1.075	3.584037	0.0385284	0.01075	Y	YN	0	0	Yyn0	4	1.075	3.584037	0.0385284	0.01075
0.4 MVA 10/0.4 kV Yyn0 6 ASEA	Three Phase Transformer	0.4	50	10	0.4	6	5	1.25	4.694677	0.05868347	0.0125	Y	YN	0	0	Yyn0	6	1.25	4.694677	0.05868347	0.0125
0.4 MVA 10/0.4 kV Yyn0 6 wnr ASEA	Three Phase Transformer	0.4	50	10	0.4	6	5	1.25	4.694677	0.05868347	0.0125	Y	YN	0	0	Yyn0	6	1.25	4.694677	0.05868347	0.0125
0.4 MVA 10/0.4 kV Yyn6 4 ASEA	Three Phase Transformer	0.4	50	10	0.4	4	4.3	1.075	3.584037	0.0385284	0.01075	Y	YN	0	6	Yyn6	4	1.075	3.584037	0.0385284	0.01075
0.4 MVA 10/0.4 kV Yyn6 4 wnr ASEA	Three Phase Transformer	0.4	50	10	0.4	4	4.3	1.075	3.584037	0.0385284	0.01075	Y	YN	0	6	Yyn6	4	1.075	3.584037	0.0385284	0.01075
0.4 MVA 10/0.4 kV Yyn6 6 ASEA	Three Phase Transformer	0.4	50	10	0.4	6	5	1.25	4.694677	0.05868347	0.0125	Y	YN	0	6	Yyn6	6	1.25	4.694677	0.05868347	0.0125
0.4 MVA 10/0.4 kV Yyn6 6 wnr ASEA	Three Phase Transformer	0.4	50	10	0.4	6	5	1.25	4.694677	0.05868347	0.0125	Y	YN	0	6	Yyn6	6	1.25	4.694677	0.05868347	0.0125
0.5 MVA 10/0.4 kV 0.94 GEAFOL	Three Phase Transformer	0.5	50	10	0.4	6	4.7	0.94	6.304159	0.05925909	0.0094	D	YN	0	5	Dyn5	6	0.9399999	6.304159	0.05925909	0.0094
0.5 MVA 10/0.4 kV 1.01 GEAFOL	Three Phase Transformer	0.5	50	10	0.4	4	4.8	0.96	4.044887	0.03883091	0.0096	D	YN	0	5	Dyn5	4	0.96	4.044887	0.03883091	0.0096
0.5 MVA 10/0.4 kV 1.2 GEAFOL	Three Phase Transformer	0.5	50	10	0.4	6	5	1	5.91608	0.0591608	0.01	D	YN	0	5	Dyn5	6	1	5.91608	0.0591608	0.01
0.5 MVA 10/0.4 kV 1.2 GEAFOL/FC	Three Phase Transformer	0.5	50	10	0.4	6	5.2	1.04	5.681903	0.05909179	0.0104	D	YN	0	5	Dyn5	6	1.04	5.681903	0.05909179	0.0104
0.5 MVA 10/0.4 kV 1.3 GEAFOL	Three Phase Transformer	0.5	50	10	0.4	4	4.2	0.84	4.655721	0.03910805	0.0084	D	YN	0	5	Dyn5	4	0.84	4.655721	0.03910805	0.0084
0.5 MVA 10/0.4 kV DOTE 500/10 SGB	Three Phase Transformer	0.5	50	10	0.4	4	5.5	1.1	3.496161	0.03845777	0.011	Y	ZN	0	5	Yzn5	4	1.1	3.496161	0.03845777	0.011
0.5 MVA 10/0.4 kV DOTEL 500/10 SGB	Three Phase Transformer	0.5	50	10	0.4	4	5.5	1.1	3.496161	0.03845777	0.011	Y	ZN	0	5	Yzn5	4	1.1	3.496161	0.03845777	0.011
0.5 MVA 10/0.4 kV DOTN 500/10 SGB	Three Phase Transformer	0.5	50	10	0.4	4	7.15	1.43	2.612345	0.03735653	0.0143	Y	ZN	0	5	Yzn5	4	1.43	2.612345	0.03735653	0.0143
0.5 MVA 10/0.4 kV DOTNL 500/10 SGB	Three Phase Transformer	0.5	50	10	0.4	4	7.15	1.43	2.612345	0.03735653	0.0143	Y	ZN	0	5	Yzn5	4	1.43	2.612345	0.03735653	0.0143
0.5 MVA 10/0.4 kV DT 500 SGB	Three Phase Transformer	0.5	50	10	0.4	4	5.4	1.08	3.566149	0.03851441	0.0108	Y	ZN	0	5	Yzn5	4	1.08	3.566149	0.03851441	0.0108
0.5 MVA 10/0.4 kV DT 500/10 F SGB	Three Phase Transformer	0.5	50	10	0.4	6	5.5	1.1	5.362095	0.05898305	0.011	Y	ZN	0	5	Yzn5	6	1.1	5.362095	0.05898305	0.011
0.5 MVA 10/0.4 kV DTTH SGB	Three Phase Transformer	0.5	50	10	0.4	4	5.1	1.02	3.791926	0.03867764	0.0102	D	YN	0	5	Dyn5	4	1.02	3.791926	0.03867764	0.0102
0.5 MVA 10/0.4 kV DTTHL SGB	Three Phase Transformer	0.5	50	10	0.4	4	5.1	1.02	3.791926	0.03867764	0.0102	D	YN	0	5	Dyn5	4	1.02	3.791926	0.03867764	0.0102
0.5 MVA 10/0.4 kV DTTHYL SGB	Three Phase Transformer	0.5	50	10	0.4	6	5.3	1.06	5.571343	0.05905624	0.0106	D	YN	0	5	Dyn5	6	1.06	5.571344	0.05905624	0.0106
0.5 MVA 10/0.4 kV Dyn1 4 ASEA	Three Phase Transformer	0.5	50	10	0.4	4	5.5	1.1	3.496161	0.03845777	0.011	D	YN	0	1	Dyn1	4	1.1	3.496161	0.03845777	0.011
0.5 MVA 10/0.4 kV Dyn1 4 wnr ASEA	Three Phase Transformer	0.5	50	10	0.4	4	5.5	1.1	3.496161	0.03845777	0.011	D	YN	0	1	Dyn1	4	1.1	3.496161	0.03845777	0.011
0.5 MVA 10/0.4 kV Dyn1 6 ASEA	Three Phase Transformer	0.5	50	10	0.4	6	5.7	1.14	5.167285	0.05890704	0.0114	D	YN	0	1	Dyn1	6	1.14	5.167284	0.05890704	0.0114
0.5 MVA 10/0.4 kV Dyn1 6 wnr ASEA	Three Phase Transformer	0.5	50	10	0.4	6	5.7	1.14	5.167285	0.05890704	0.0114	D	YN	0	1	Dyn1	6	1.14	5.167284	0.05890704	0.0114
0.5 MVA 10/0.4 kV Dyn11 4 ASEA	Three Phase Transformer	0.5	50	10	0.4	4	5.5	1.1	3.496161	0.03845777	0.011	D	YN	0	11	Dyn11	4	1.1	3.496161	0.03845777	0.011
0.5 MVA 10/0.4 kV Dyn11 4 wnr ASEA	Three Phase Transformer	0.5	50	10	0.4	4	5.5	1.1	3.496161	0.03845777	0.011	D	YN	0	11	Dyn11	4	1.1	3.496161	0.03845777	0.011
0.5 MVA 10/0.4 kV Dyn11 6 ASEA	Three Phase Transformer	0.5	50	10	0.4	6	5.7	1.14	5.167285	0.05890704	0.0114	D	YN	0	11	Dyn11	6	1.14	5.167284	0.05890704	0.0114
0.5 MVA 10/0.4 kV Dyn11 6 wnr ASEA	Three Phase Transformer	0.5	50	10	0.4	6	5.7	1.14	5.167285	0.05890704	0.0114	D	YN	0	11	Dyn11	6	1.14	5.167284	0.05890704	0.0114
0.5 MVA 10/0.4 kV Dyn5 4 ASEA	Three Phase Transformer	0.5	50	10	0.4	4	5.5	1.1	3.496161	0.03845777	0.011	D	YN	0	5	Dyn5	4	1.1	3.496161	0.03845777	0.011
0.5 MVA 10/0.4 kV Dyn5 4 wnr ASEA	Three Phase Transformer	0.5	50	10	0.4	4	5.5	1.1	3.496161	0.03845777	0.011	D	YN	0	5	Dyn5	4	1.1	3.496161	0.03845777	0.011
0.5 MVA 10/0.4 kV Dyn5 6 ASEA	Three Phase Transformer	0.5	50	10	0.4	6	5.7	1.14	5.167285	0.05890704	0.0114	D	YN	0	5	Dyn5	6	1.14	5.167284	0.05890704	0.0114
0.5 MVA 10/0.4 kV Dyn5 6 wnr ASEA	Three Phase Transformer	0.5	50	10	0.4	6	5.7	1.14	5.167285	0.05890704	0.0114	D	YN	0	5	Dyn5	6	1.14	5.167284	0.05890704	0.0114
0.5 MVA 10/0.4 kV Dyn7 4 ASEA	Three Phase Transformer	0.5	50	10	0.4	4	5.5	1.1	3.496161	0.03845777	0.011	D	YN	0	7	Dyn7	4	1.1	3.496161	0.03845777	0.011
0.5 MVA 10/0.4 kV Dyn7 4 wnr ASEA	Three Phase Transformer	0.5	50	10	0.4	4	5.5	1.1	3.496161	0.03845777	0.011	D	YN	0	7	Dyn7	4	1.1	3.496161	0.03845777	0.011
0.5 MVA 10/0.4 kV Dyn7 6 ASEA	Three Phase Transformer	0.5	50	10	0.4	6	5.7	1.14	5.167285	0.05890704	0.0114	D	YN	0	7	Dyn7	6	1.14	5.167284	0.05890704	0.0114
0.5 MVA 10/0.4 kV Dyn7 6 wnr ASEA	Three Phase Transformer	0.5	50	10	0.4	6	5.7	1.14	5.167285	0.05890704	0.0114	D	YN	0	7	Dyn7	6	1.14	5.167284	0.05890704	0.0114
0.5 MVA 10/0.4 kV Trafo Union	Three Phase Transformer	0.5	50	10	0.4	4	5.2	1.04	3.713879	0.03862434	0.0104	D	YN	0	5	Dyn5	4	1.04	3.713879	0.03862434	0.0104
0.5 MVA 10/0.4 kV Trafo Union wnr	Three Phase Transformer	0.5	50	10	0.4	4	5.5	1.1	3.496161	0.03845777	0.011	D	YN	0	5	Dyn5	4	1.1	3.496161	0.03845777	0.011
0.5 MVA 10/0.4 kV Yyn0 4 ASEA	Three Phase Transformer	0.5	50	10	0.4	4	5.5	1.1	3.496161	0.03845777	0.011	Y	YN	0	0	Yyn0	4	1.1	3.496161	0.03845777	0.011
0.5 MVA 10/0.4 kV Yyn0 4 wnr ASEA	Three Phase Transformer	0.5	50	10	0.4	4	5.5	1.1	3.496161	0.03845777	0.011	Y	YN	0	0	Yyn0	4	1.1	3.496161	0.03845777	0.011
0.5 MVA 10/0.4 kV Yyn0 6 ASEA	Three Phase Transformer	0.5	50	10	0.4	6	5.7	1.14	5.167285	0.05890704	0.0114	Y	YN	0	0	Yyn0	6	1.14	5.167284	0.05890704	0.0114
0.5 MVA 10/0.4 kV Yyn0 6 wnr ASEA	Three Phase Transformer	0.5	50	10	0.4	6	5.7	1.14	5.167285	0.05890704	0.0114	Y	YN	0	0	Yyn0	6	1.14	5.167284	0.05890704	0.0114
0.5 MVA 10/0.4 kV Yyn6 4 ASEA	Three Phase Transformer	0.5	50	10	0.4	4	5.5	1.1	3.496161	0.03845777	0.011	Y	YN	0	6	Yyn6	4	1.1	3.496161	0.03845777	0.011
0.5 MVA 10/0.4 kV Yyn6 4 wnr ASEA	Three Phase Transformer	0.5	50	10	0.4	4	5.5	1.1	3.496161	0.03845777	0.011	Y	YN	0	6	Yyn6	4	1.1	3.496161	0.03845777	0.011
0.5 MVA 10/0.4 kV Yyn6 6 ASEA	Three Phase Transformer	0.5	50	10	0.4	6	5.7	1.14	5.167285	0.05890704	0.0114	Y	YN	0	6	Yyn6	6	1.14	5.167284	0.05890704	0.0114
0.5 MVA 10/0.4 kV Yyn6 6 wnr ASEA	Three Phase Transformer	0.5	50	10	0.4	6	5.7	1.14	5.167285	0.05890704	0.0114	Y	YN	0	6	Yyn6	6	1.14	5.167284	0.05890704	0.0114
0.63 MVA 10/0.4 kV 1.09 GEAFOL	Three Phase Transformer	0.63	50	10	0.4	6	6.4	1.015873	5.820978	0.05913375	0.01015873	D	YN	0	5	Dyn5	6	1.015873	5.820978	0.05913375	0.01015873
0.63 MVA 10/0.4 kV 1.17 GEAFOL	Three Phase Transformer	0.63	50	10	0.4	4	6.4	1.015873	3.808399	0.0386885	0.01015873	D	YN	0	5	Dyn5	4	1.015873	3.808399	0.0386885	0.01015873
0.63 MVA 10/0.4 kV 1.4 GEAFOL	Three Phase Transformer	0.63	50	10	0.4	6	5.6	0.8888889	6.675515	0.05933791	0.00888889	D	YN	0	5	Dyn5	6	0.8888889	6.675515	0.05933791	0.00888889
0.63 MVA 10/0.4 kV 1.4 GEAFOL/FC	Three Phase Transformer	0.63	50	10	0.4	6	6.1	0.968254	6.115501	0.05921358	0.00968254	D	YN	0	5	Dyn5	6	0.968254	6.115501	0.05921358	0.00968254
0.63 MVA 10/0.4 kV 1.5 GEAFOL	Three Phase Transformer	0.63	50	10	0.4	4	5.8	0.920635	4.228182	0.03892612	0.00920635	D	YN	0	5	Dyn5	4	0.920635	4.228182	0.03892612	0.00920635
0.63 MVA 10/0.4 kV DOTE 630/10 SGB	Three Phase Transformer	0.63	50	10	0.4	4	6.5	1.031746	3.745735	0.03864647	0.01031746	Y	ZN	0	5	Yzn5	4	1.031746	3.745735	0.03864647	0.01031746
0.63 MVA 10/0.4 kV DOTEL 630/10 SGB	Three Phase Transformer	0.63	50	10	0.4	4	6.5	1.031746	3.745735	0.03864647	0.01031746	Y	ZN	0	5	Yzn5	4	1.031746	3.745735	0.03864647	0.01031746
0.63 MVA 10/0.4 kV DOTN 630/10 SGB	Three Phase Transformer	0.63	50	10	0.4	4	8.4	1.333333	2.828427	0.03771236	0.01333333	Y	ZN	0	5	Yzn5	4	1.333333	2.828428	0.03771236	0.01333333
0.63 MVA 10/0.4 kV DOTNL 630/10 SGB	Three Phase Transformer	0.63	50	10	0.4	4	8.4	1.333333	2.828427	0.03771236	0.01333333	Y	ZN	0	5	Yzn5	4	1.333333	2.828428	0.03771236	0.01333333
0.63 MVA 10/0.4 kV DT 630 SGB	Three Phase Transformer	0.63	50	10	0.4	4	6.6	1.047619	3.684903	0.03860375	0.01047619	Y	ZN	0	5	Yzn5	4	1.047619	3.684904	0.03860375	0.01047619
0.63 MVA 10/0.4 kV DT 630/10 F SGB	Three Phase Transformer	0.63	50	10	0.4	6	6.5	1.031746	5.72876	0.05910626	0.01031746	Y	ZN	0	5	Yzn5	6	1.031746	5.72876	0.05910626	0.01031746
0.63 MVA 10/0.4 kV DTKa SGB	Three Phase Transformer	0.63	50	10	0.4	6	6.5	1.031746	5.72876	0.05910626	0.01031746	Y	ZN	0	5	Yzn5	6	1.031746	5.72876	0.05910626	0.01031746
0.63 MVA 10/0.4 kV DTTH SGB	Three Phase Transformer	0.63	50	10	0.4	4	6.4	1.015873	3.808399	0.0386885	0.01015873	D	YN	0	5	Dyn5	4	1.015873	3.808399	0.0386885	0.01015873
0.63 MVA 10/0.4 kV DTTHL SGB	Three Phase Transformer	0.63	50	10	0.4	4	6.4	1.015873	3.808399	0.0386885	0.01015873	D	YN	0	5	Dyn5	4	1.015873	3.808399	0.0386885	0.01015873
0.63 MVA 10/0.4 kV DTTHYL SGB	Three Phase Transformer	0.63	50	10	0.4	6	6	0.952381	6.220128	0.05923932	0.00952381	D	YN	0	5	Dyn5	6	0.952381	6.220128	0.05923932	0.00952381
0.63 MVA 10/0.4 kV Dyn1 4 ASEA	Three Phase Transformer	0.63	50	10	0.4	4	6.4	1.015873	3.808399	0.0386885	0.01015873	D	YN	0	1	Dyn1	4	1.015873	3.808399	0.0386885	0.01015873
0.63 MVA 10/0.4 kV Dyn1 4 wnr ASEA	Three Phase Transformer	0.63	50	10	0.4	4	6.4	1.015873	3.808399	0.0386885	0.01015873	D	YN	0	1	Dyn1	4	1.015873	3.808399	0.0386885	0.01015873
0.63 MVA 10/0.4 kV Dyn1 6 ASEA	Three Phase Transformer	0.63	50	10	0.4	6	6.6	1.047619	5.639295	0.05907833	0.01047619	D	YN	0	1	Dyn1	6	1.047619	5.639296	0.05907833	0.01047619
0.63 MVA 10/0.4 kV Dyn1 6 wnr ASEA	Three Phase Transformer	0.63	50	10	0.4	6	6.6	1.047619	5.639295	0.05907833	0.01047619	D	YN	0	1	Dyn1	6	1.047619	5.639296	0.05907833	0.01047619
0.63 MVA 10/0.4 kV Dyn11 4 ASEA	Three Phase Transformer	0.63	50	10	0.4	4	6.4	1.015873	3.808399	0.0386885	0.01015873	D	YN	0	11	Dyn11	4	1.015873	3.808399	0.0386885	0.01015873
0.63 MVA 10/0.4 kV Dyn11 4wnr ASEA	Three Phase Transformer	0.63	50	10	0.4	4	6.4	1.015873	3.808399	0.0386885	0.01015873	D	YN	0	11	Dyn11	4	1.015873	3.808399	0.0386885	0.01015873
0.63 MVA 10/0.4 kV Dyn11 6 ASEA	Three Phase Transformer	0.63	50	10	0.4	6	6.6	1.047619	5.639295	0.05907833	0.01047619	D	YN	0	11	Dyn11	6	1.047619	5.639296	0.05907833	0.01047619
0.63 MVA 10/0.4 kV Dyn11 6 wnr ASEA	Three Phase Transformer	0.63	50	10	0.4	6	6.6	1.047619	5.639295	0.05907833	0.01047619	D	YN	0	11	Dyn11	6	1.047619	5.639296	0.05907833	0.01047619
0.63 MVA 10/0.4 kV Dyn5 4 ASEA	Three Phase Transformer	0.63	50	10	0.4	4	6.4	1.015873	3.808399	0.0386885	0.01015873	D	YN	0	5	Dyn5	4	1.015873	3.808399	0.0386885	0.01015873
0.63 MVA 10/0.4 kV Dyn5 4 wnr ASEA	Three Phase Transformer	0.63	50	10	0.4	4	6.4	1.015873	3.808399	0.0386885	0.01015873	D	YN	0	5	Dyn5	4	1.015873	3.808399	0.0386885	0.01015873
0.63 MVA 10/0.4 kV Dyn5 6 ASEA	Three Phase Transformer	0.63	50	10	0.4	6	6.6	1.047619	5.639295	0.05907833	0.01047619	D	YN	0	5	Dyn5	6	1.047619	5.639296	0.05907833	0.01047619
0.63 MVA 10/0.4 kV Dyn5 6 wnr ASEA	Three Phase Transformer	0.63	50	10	0.4	6	6.6	1.047619	5.639295	0.05907833	0.01047619	D	YN	0	5	Dyn5	6	1.047619	5.639296	0.05907833	0.01047619
0.63 MVA 10/0.4 kV Dyn7 4 ASEA	Three Phase Transformer	0.63	50	10	0.4	4	6.4	1.015873	3.808399	0.0386885	0.01015873	D	YN	0	7	Dyn7	4	1.015873	3.808399	0.0386885	0.01015873
0.63 MVA 10/0.4 kV Dyn7 4 wnr ASEA	Three Phase Transformer	0.63	50	10	0.4	4	6.4	1.015873	3.808399	0.0386885	0.01015873	D	YN	0	7	Dyn7	4	1.015873	3.808399	0.0386885	0.01015873
0.63 MVA 10/0.4 kV Dyn7 6 ASEA	Three Phase Transformer	0.63	50	10	0.4	6	6.6	1.047619	5.639295	0.05907833	0.01047619	D	YN	0	7	Dyn7	6	1.047619	5.639296	0.05907833	0.01047619
0.63 MVA 10/0.4 kV Dyn7 6 wnr ASEA	Three Phase Transformer	0.63	50	10	0.4	6	6.6	1.047619	5.639295	0.05907833	0.01047619	D	YN	0	7	Dyn7	6	1.047619	5.639296	0.05907833	0.01047619
0.63 MVA 10/0.4 kV Trafo Union	Three Phase Transformer	0.63	50	10	0.4	4	6.3	1	3.872983	0.03872983	0.01	D	YN	0	5	Dyn5	4	1	3.872983	0.03872983	0.01
0.63 MVA 10/0.4 kV Trafo Union wnr	Three Phase Transformer	0.63	50	10	0.4	4	6.8	1.079365	3.568412	0.03851619	0.01079365	D	YN	0	5	Dyn5	4	1.079365	3.568412	0.03851619	0.01079365
0.63 MVA 10/0.4 kV Yyn0 4 ASEA	Three Phase Transformer	0.63	50	10	0.4	4	6.4	1.015873	3.808399	0.0386885	0.01015873	Y	YN	0	0	Yyn0	4	1.015873	3.808399	0.0386885	0.01015873
0.63 MVA 10/0.4 kV Yyn0 4 wnr ASEA	Three Phase Transformer	0.63	50	10	0.4	4	6.4	1.015873	3.808399	0.0386885	0.01015873	Y	YN	0	0	Yyn0	4	1.015873	3.808399	0.0386885	0.01015873
0.63 MVA 10/0.4 kV Yyn0 6 ASEA	Three Phase Transformer	0.63	50	10	0.4	6	6.6	1.047619	5.639295	0.05907833	0.01047619	Y	YN	0	0	Yyn0	6	1.047619	5.639296	0.05907833	0.01047619
0.63 MVA 10/0.4 kV Yyn0 6wnr ASEA	Three Phase Transformer	0.63	50	10	0.4	6	6.6	1.047619	5.639295	0.05907833	0.01047619	Y	YN	0	0	Yyn0	6	1.047619	5.639296	0.05907833	0.01047619
0.63 MVA 10/0.4 kV Yyn6 4 ASEA	Three Phase Transformer	0.63	50	10	0.4	4	6.4	1.015873	3.808399	0.0386885	0.01015873	Y	YN	0	6	Yyn6	4	1.015873	3.808399	0.0386885	0.01015873
0.63 MVA 10/0.4 kV Yyn6 4 wnr ASEA	Three Phase Transformer	0.63	50	10	0.4	4	6.4	1.015873	3.808399	0.0386885	0.01015873	Y	YN	0	6	Yyn6	4	1.015873	3.808399	0.0386885	0.01015873
0.63 MVA 10/0.4 kV Yyn6 6 ASEA	Three Phase Transformer	0.63	50	10	0.4	6	6.6	1.047619	5.639295	0.05907833	0.01047619	Y	YN	0	6	Yyn6	6	1.047619	5.639296	0.05907833	0.01047619
0.63 MVA 10/0.4 kV Yyn6 6 wnr ASEA	Three Phase Transformer	0.63	50	10	0.4	6	6.6	1.047619	5.639295	0.05907833	0.01047619	Y	YN	0	6	Yyn6	6	1.047619	5.639296	0.05907833	0.01047619
0.8 MVA 10/0.4 kV 1.33 GEAFOL	Three Phase Transformer	0.8	50	10	0.4	6	7.7	0.9625	6.153035	0.05922296	0.009625	D	YN	0	5	Dyn5	6	0.9625	6.153035	0.05922296	0.009625
0.8 MVA 10/0.4 kV 1.4 GEAFOL	Three Phase Transformer	0.8	50	10	0.4	4	7.7	0.9625	4.033738	0.03882473	0.009625	D	YN	0	5	Dyn5	4	0.9625	4.033738	0.03882473	0.009625
0.8 MVA 10/0.4 kV 1.7 GEAFOL	Three Phase Transformer	0.8	50	10	0.4	6	6.6	0.825	7.203649	0.0594301	0.00825	D	YN	0	5	Dyn5	6	0.825	7.203649	0.0594301	0.00825
0.8 MVA 10/0.4 kV 1.7 GEAFOL/FC	Three Phase Transformer	0.8	50	10	0.4	6	6.8	0.85	6.98763	0.05939486	0.0085	D	YN	0	5	Dyn5	6	0.85	6.98763	0.05939486	0.0085
0.8 MVA 10/0.4 kV 1.8 GEAFOL	Three Phase Transformer	0.8	50	10	0.4	4	6.6	0.825	4.744239	0.03913997	0.00825	D	YN	0	5	Dyn5	4	0.825	4.744239	0.03913997	0.00825
0.8 MVA 10/0.4 kV DOTE 800/10 SGB	Three Phase Transformer	0.8	50	10	0.4	6	8.5	1.0625	5.557812	0.05905175	0.010625	Y	ZN	0	5	Yzn5	6	1.0625	5.557812	0.05905175	0.010625
0.8 MVA 10/0.4 kV DOTEL 800/10 SGB	Three Phase Transformer	0.8	50	10	0.4	6	8.5	1.0625	5.557812	0.05905175	0.010625	Y	ZN	0	5	Yzn5	6	1.0625	5.557812	0.05905175	0.010625
0.8 MVA 10/0.4 kV DT 800/10 F SGB	Three Phase Transformer	0.8	50	10	0.4	6	7.8	0.975	6.072052	0.05920251	0.00975	Y	ZN	0	5	Yzn5	6	0.975	6.072052	0.05920251	0.00975
0.8 MVA 10/0.4 kV DTTH SGB	Three Phase Transformer	0.8	50	10	0.4	6	7.5	0.9374999	6.321393	0.05926305	0.009375	D	YN	0	5	Dyn5	6	0.9375	6.321392	0.05926305	0.009375
0.8 MVA 10/0.4 kV DTTHIL SGB	Three Phase Transformer	0.8	50	10	0.4	6	5	0.625	9.547774	0.05967359	0.00625	D	YN	0	5	Dyn5	6	0.625	9.547774	0.05967359	0.00625
0.8 MVA 10/0.4 kV DTTHL SGB	Three Phase Transformer	0.8	50	10	0.4	6	7	0.875	6.783834	0.05935855	0.00875	D	YN	0	5	Dyn5	6	0.875	6.783834	0.05935855	0.00875
0.8 MVA 10/0.4 kV Dyn1 ASEA	Three Phase Transformer	0.8	50	10	0.4	6	7.7	0.9625	6.153035	0.05922296	0.009625	D	YN	0	1	Dyn1	6	0.9625	6.153035	0.05922296	0.009625
0.8 MVA 10/0.4 kV Dyn1 wnr ASEA	Three Phase Transformer	0.8	50	10	0.4	6	7.7	0.9625	6.153035	0.05922296	0.009625	D	YN	0	1	Dyn1	6	0.9625	6.153035	0.05922296	0.009625
0.8 MVA 10/0.4 kV Dyn11 ASEA	Three Phase Transformer	0.8	50	10	0.4	6	7.7	0.9625	6.153035	0.05922296	0.009625	D	YN	0	11	Dyn11	6	0.9625	6.153035	0.05922296	0.009625
0.8 MVA 10/0.4 kV Dyn11 wnr ASEA	Three Phase Transformer	0.8	50	10	0.4	6	7.7	0.9625	6.153035	0.05922296	0.009625	D	YN	0	11	Dyn11	6	0.9625	6.153035	0.05922296	0.009625
0.8 MVA 10/0.4 kV Dyn5 ASEA	Three Phase Transformer	0.8	50	10	0.4	6	7.7	0.9625	6.153035	0.05922296	0.009625	D	YN	0	5	Dyn5	6	0.9625	6.153035	0.05922296	0.009625
0.8 MVA 10/0.4 kV Dyn5 wnr ASEA	Three Phase Transformer	0.8	50	10	0.4	6	7.7	0.9625	6.153035	0.05922296	0.009625	D	YN	0	5	Dyn5	6	0.9625	6.153035	0.05922296	0.009625
0.8 MVA 10/0.4 kV Dyn7 ASEA	Three Phase Transformer	0.8	50	10	0.4	6	7.7	0.9625	6.153035	0.05922296	0.009625	D	YN	0	7	Dyn7	6	0.9625	6.153035	0.05922296	0.009625
0.8 MVA 10/0.4 kV Dyn7 wnr ASEA	Three Phase Transformer	0.8	50	10	0.4	6	7.7	0.9625	6.153035	0.05922296	0.009625	D	YN	0	7	Dyn7	6	0.9625	6.153035	0.05922296	0.009625
0.8 MVA 10/0.4 kV Trafo Union	Three Phase Transformer	0.8	50	10	0.4	6	6.9	0.8625	6.884272	0.05937684	0.008625	D	YN	0	5	Dyn5	6	0.8625	6.884272	0.05937684	0.008625
0.8 MVA 10/0.4 kV Trafo Union wnr	Three Phase Transformer	0.8	50	10	0.4	6	7	0.875	6.783834	0.05935855	0.00875	D	YN	0	5	Dyn5	6	0.875	6.783834	0.05935855	0.00875
0.8 MVA 10/0.4 kV Yyn0 ASEA	Three Phase Transformer	0.8	50	10	0.4	6	7.7	0.9625	6.153035	0.05922296	0.009625	Y	YN	0	0	Yyn0	6	0.9625	6.153035	0.05922296	0.009625
0.8 MVA 10/0.4 kV Yyn0 wnr ASEA	Three Phase Transformer	0.8	50	10	0.4	6	7.7	0.9625	6.153035	0.05922296	0.009625	Y	YN	0	0	Yyn0	6	0.9625	6.153035	0.05922296	0.009625
0.8 MVA 10/0.4 kV Yyn6 ASEA	Three Phase Transformer	0.8	50	10	0.4	6	7.7	0.9625	6.153035	0.05922296	0.009625	Y	YN	0	6	Yyn6	6	0.9625	6.153035	0.05922296	0.009625
0.8 MVA 10/0.4 kV Yyn6 wnr ASEA	Three Phase Transformer	0.8	50	10	0.4	6	7.7	0.9625	6.153035	0.05922296	0.009625	Y	YN	0	6	Yyn6	6	0.9625	6.153035	0.05922296	0.009625
1 MVA 10/0.4 kV 1.56 GEAFOL	Three Phase Transformer	1	50	10	0.4	6	8.2	0.82	7.248418	0.05943703	0.0082	D	YN	0	5	Dyn5	6	0.82	7.248418	0.05943703	0.0082
1 MVA 10/0.4 kV 1.6 GEAFOL	Three Phase Transformer	1	50	10	0.4	4	9.2	0.92	4.231264	0.03892763	0.0092	D	YN	0	5	Dyn5	4	0.92	4.231264	0.03892763	0.0092
1 MVA 10/0.4 kV 2 GEAFOL	Three Phase Transformer	1	50	10	0.4	6	7.9	0.7900001	7.528815	0.05947764	0.0079	D	YN	0	5	Dyn5	6	0.79	7.528815	0.05947764	0.0079
1 MVA 10/0.4 kV 2 GEAFOL/FC	Three Phase Transformer	1	50	10	0.4	6	8	0.8	7.433034	0.05946428	0.008	D	YN	0	5	Dyn5	6	0.8	7.433034	0.05946428	0.008
1 MVA 10/0.4 kV 2.1 GEAFOL	Three Phase Transformer	1	50	10	0.4	4	7.5	0.75	5.238745	0.03929058	0.0075	D	YN	0	5	Dyn5	4	0.75	5.238745	0.03929058	0.0075
1 MVA 10/0.4 kV DOTE 1000/10 SGB	Three Phase Transformer	1	50	10	0.4	6	10.5	1.05	5.626105	0.0590741	0.0105	Y	ZN	0	5	Yzn5	6	1.05	5.626105	0.0590741	0.0105
1 MVA 10/0.4 kV DOTEL 1000/10 SGB	Three Phase Transformer	1	50	10	0.4	6	10.5	1.05	5.626105	0.0590741	0.0105	Y	ZN	0	5	Yzn5	6	1.05	5.626105	0.0590741	0.0105
1 MVA 10/0.4 kV DT 1000 SGB	Three Phase Transformer	1	50	10	0.4	5.5	8.2	0.82	6.632352	0.05438529	0.0082	Y	ZN	0	5	Yzn5	5.5	0.82	6.632352	0.05438529	0.0082
1 MVA 10/0.4 kV DT 1000/10 F SGB	Three Phase Transformer	1	50	10	0.4	6	9.5	0.95	6.236121	0.05924314	0.0095	Y	ZN	0	5	Yzn5	6	0.95	6.236121	0.05924314	0.0095
1 MVA 10/0.4 kV DTKa SGB	Three Phase Transformer	1	50	10	0.4	6	8.7	0.87	6.823667	0.0593659	0.0087	Y	ZN	0	5	Yzn5	6	0.87	6.823667	0.0593659	0.0087
1 MVA 10/0.4 kV DTTH SGB	Three Phase Transformer	1	50	10	0.4	6	8.8	0.88	6.74445	0.05935116	0.0088	D	YN	0	5	Dyn5	6	0.88	6.74445	0.05935116	0.0088
1 MVA 10/0.4 kV DTTHIL SGB	Three Phase Transformer	1	50	10	0.4	6	6.1	0.61	9.785101	0.05968911	0.0061	D	YN	0	5	Dyn5	6	0.61	9.7851	0.05968911	0.0061
1 MVA 10/0.4 kV DTTHL SGB	Three Phase Transformer	1	50	10	0.4	6	8.2	0.82	7.248418	0.05943703	0.0082	D	YN	0	5	Dyn5	6	0.82	7.248418	0.05943703	0.0082
1 MVA 10/0.4 kV Dyn1 ASEA	Three Phase Transformer	1	50	10	0.4	6	8.8	0.88	6.74445	0.05935116	0.0088	D	YN	0	1	Dyn1	6	0.88	6.74445	0.05935116	0.0088
1 MVA 10/0.4 kV Dyn1 wnr ASEA	Three Phase Transformer	1	50	10	0.4	6	8.8	0.88	6.74445	0.05935116	0.0088	D	YN	0	1	Dyn1	6	0.88	6.74445	0.05935116	0.0088
1 MVA 10/0.4 kV Dyn11 ASEA	Three Phase Transformer	1	50	10	0.4	6	8.8	0.88	6.74445	0.05935116	0.0088	D	YN	0	11	Dyn11	6	0.88	6.74445	0.05935116	0.0088
1 MVA 10/0.4 kV Dyn11 wnr ASEA	Three Phase Transformer	1	50	10	0.4	6	8.8	0.88	6.74445	0.05935116	0.0088	D	YN	0	11	Dyn11	6	0.88	6.74445	0.05935116	0.0088
1 MVA 10/0.4 kV Dyn5 ASEA	Three Phase Transformer	1	50	10	0.4	6	8.8	0.88	6.74445	0.05935116	0.0088	D	YN	0	5	Dyn5	6	0.88	6.74445	0.05935116	0.0088
1 MVA 10/0.4 kV Dyn5 wnr ASEA	Three Phase Transformer	1	50	10	0.4	6	8.8	0.88	6.74445	0.05935116	0.0088	D	YN	0	5	Dyn5	6	0.88	6.74445	0.05935116	0.0088
1 MVA 10/0.4 kV Dyn7 ASEA	Three Phase Transformer	1	50	10	0.4	6	8.8	0.88	6.74445	0.05935116	0.0088	D	YN	0	7	Dyn7	6	0.88	6.74445	0.05935116	0.0088
1 MVA 10/0.4 kV Dyn7 wnr ASEA	Three Phase Transformer	1	50	10	0.4	6	8.8	0.88	6.74445	0.05935116	0.0088	D	YN	0	7	Dyn7	6	0.88	6.74445	0.05935116	0.0088
1 MVA 10/0.4 kV Trafo Union	Three Phase Transformer	1	50	10	0.4	6	8.3	0.83	7.159415	0.05942314	0.0083	D	YN	0	5	Dyn5	6	0.83	7.159415	0.05942314	0.0083
1 MVA 10/0.4 kV Trafo Union wnr	Three Phase Transformer	1	50	10	0.4	6	8.7	0.87	6.823667	0.0593659	0.0087	D	YN	0	5	Dyn5	6	0.87	6.823667	0.0593659	0.0087
1 MVA 10/0.4 kV Yyn0 ASEA	Three Phase Transformer	1	50	10	0.4	6	8.8	0.88	6.74445	0.05935116	0.0088	Y	YN	0	0	Yyn0	6	0.88	6.74445	0.05935116	0.0088
1 MVA 10/0.4 kV Yyn0 wnr ASEA	Three Phase Transformer	1	50	10	0.4	6	8.8	0.88	6.74445	0.05935116	0.0088	Y	YN	0	0	Yyn0	6	0.88	6.74445	0.05935116	0.0088
1 MVA 10/0.4 kV Yyn6 ASEA	Three Phase Transformer	1	50	10	0.4	6	8.8	0.88	6.74445	0.05935116	0.0088	Y	YN	0	6	Yyn6	6	0.88	6.74445	0.05935116	0.0088
1 MVA 10/0.4 kV Yyn6 wnr ASEA	Three Phase Transformer	1	50	10	0.4	6	8.8	0.88	6.74445	0.05935116	0.0088	Y	YN	0	6	Yyn6	6	0.88	6.74445	0.05935116	0.0088
1.25 MVA 10/0.4 kV 1.87 GEAFOL	Three Phase Transformer	1.25	50	10	0.4	6	9.1	0.728	8.180866	0.05955671	0.00728	D	YN	0	5	Dyn5	6	0.728	8.180866	0.05955671	0.00728
1.25 MVA 10/0.4 kV 2.4 GEAFOL	Three Phase Transformer	1.25	50	10	0.4	6	8.8	0.704	8.463857	0.05958555	0.00704	D	YN	0	5	Dyn5	6	0.704	8.463857	0.05958555	0.00704
1.25 MVA 10/0.4 kV 2.4 GEAFOL/FC	Three Phase Transformer	1.25	50	10	0.4	6	9.5	0.76	7.831147	0.05951672	0.0076	D	YN	0	5	Dyn5	6	0.76	7.831147	0.05951672	0.0076
1.25 MVA 10/0.4 kV DOTE 1250/10 SGB	Three Phase Transformer	1.25	50	10	0.4	6	13.5	1.08	5.464815	0.05902	0.0108	Y	ZN	0	5	Yzn5	6	1.08	5.464815	0.05902	0.0108
1.25 MVA 10/0.4 kV DOTEL 1250/10 SGB	Three Phase Transformer	1.25	50	10	0.4	6	13.5	1.08	5.464815	0.05902	0.0108	Y	ZN	0	5	Yzn5	6	1.08	5.464815	0.05902	0.0108
1.25 MVA 10/0.4 kV DT 1250/10 F SGB	Three Phase Transformer	1.25	50	10	0.4	6	11	0.88	6.74445	0.05935116	0.0088	Y	ZN	0	5	Yzn5	6	0.88	6.74445	0.05935116	0.0088
1.25 MVA 10/0.4 kV DTTH SGB	Three Phase Transformer	1.25	50	10	0.4	6	10.9	0.8719999	6.80768	0.05936296	0.00872	D	YN	0	5	Dyn5	6	0.872	6.80768	0.05936296	0.00872
1.25 MVA 10/0.4 kV DTTHIL SGB	Three Phase Transformer	1.25	50	10	0.4	6	7.5	0.6	9.949874	0.05969924	0.006	D	YN	0	5	Dyn5	6	0.6	9.949874	0.05969924	0.006
1.25 MVA 10/0.4 kV DTTHL SGB	Three Phase Transformer	1.25	50	10	0.4	6	10.5	0.84	7.072511	0.05940909	0.0084	D	YN	0	5	Dyn5	6	0.84	7.072511	0.05940909	0.0084
1.25 MVA 10/0.4 kV Dyn1 ASEA	Three Phase Transformer	1.25	50	10	0.4	6	10.5	0.84	7.072511	0.05940909	0.0084	D	YN	0	1	Dyn1	6	0.84	7.072511	0.05940909	0.0084
1.25 MVA 10/0.4 kV Dyn1 wnr ASEA	Three Phase Transformer	1.25	50	10	0.4	6	10.5	0.84	7.072511	0.05940909	0.0084	D	YN	0	1	Dyn1	6	0.84	7.072511	0.05940909	0.0084
1.25 MVA 10/0.4 kV Dyn11 ASEA	Three Phase Transformer	1.25	50	10	0.4	6	10.5	0.84	7.072511	0.05940909	0.0084	D	YN	0	11	Dyn11	6	0.84	7.072511	0.05940909	0.0084
1.25 MVA 10/0.4 kV Dyn11 wnr ASEA	Three Phase Transformer	1.25	50	10	0.4	6	10.5	0.84	7.072511	0.05940909	0.0084	D	YN	0	11	Dyn11	6	0.84	7.072511	0.05940909	0.0084
1.25 MVA 10/0.4 kV Dyn5 ASEA	Three Phase Transformer	1.25	50	10	0.4	6	10.5	0.84	7.072511	0.05940909	0.0084	D	YN	0	5	Dyn5	6	0.84	7.072511	0.05940909	0.0084
1.25 MVA 10/0.4 kV Dyn5 wnr ASEA	Three Phase Transformer	1.25	50	10	0.4	6	10.5	0.84	7.072511	0.05940909	0.0084	D	YN	0	5	Dyn5	6	0.84	7.072511	0.05940909	0.0084
1.25 MVA 10/0.4 kV Dyn7 ASEA	Three Phase Transformer	1.25	50	10	0.4	6	10.5	0.84	7.072511	0.05940909	0.0084	D	YN	0	7	Dyn7	6	0.84	7.072511	0.05940909	0.0084
1.25 MVA 10/0.4 kV Dyn7 wnr ASEA	Three Phase Transformer	1.25	50	10	0.4	6	10.5	0.84	7.072511	0.05940909	0.0084	D	YN	0	7	Dyn7	6	0.84	7.072511	0.05940909	0.0084
1.25 MVA 10/0.4 kV Trafo Union	Three Phase Transformer	1.25	50	10	0.4	6	10.2	0.816	7.284624	0.05944253	0.00816	D	YN	0	5	Dyn5	6	0.816	7.284624	0.05944253	0.00816
1.25 MVA 10/0.4 kV Trafo Union wnr	Three Phase Transformer	1.25	50	10	0.4	6	10.7	0.856	6.937645	0.05938625	0.00856	D	YN	0	5	Dyn5	6	0.856	6.937645	0.05938625	0.00856
1.25 MVA 10/0.4 kV Yyn0 ASEA	Three Phase Transformer	1.25	50	10	0.4	6	10.5	0.84	7.072511	0.05940909	0.0084	Y	YN	0	0	Yyn0	6	0.84	7.072511	0.05940909	0.0084
1.25 MVA 10/0.4 kV Yyn0 wnr ASEA	Three Phase Transformer	1.25	50	10	0.4	6	10.5	0.84	7.072511	0.05940909	0.0084	Y	YN	0	0	Yyn0	6	0.84	7.072511	0.05940909	0.0084
1.25 MVA 10/0.4 kV Yyn6 ASEA	Three Phase Transformer	1.25	50	10	0.4	6	10.5	0.84	7.072511	0.05940909	0.0084	Y	YN	0	6	Yyn6	6	0.84	7.072511	0.05940909	0.0084
1.25 MVA 10/0.4 kV Yyn6 wnr ASEA	Three Phase Transformer	1.25	50	10	0.4	6	10.5	0.84	7.072511	0.05940909	0.0084	Y	YN	0	6	Yyn6	6	0.84	7.072511	0.05940909	0.0084
1.6 MVA 10/0.4 kV 2.18 GEAFOL	Three Phase Transformer	1.6	50	10	0.4	6	10.9	0.68125	8.750384	0.05961199	0.0068125	D	YN	0	5	Dyn5	6	0.68125	8.750384	0.05961199	0.0068125
1.6 MVA 10/0.4 kV 2.8 GEAFOL	Three Phase Transformer	1.6	50	10	0.4	6	10.5	0.65625	9.088005	0.05964003	0.0065625	D	YN	0	5	Dyn5	6	0.65625	9.088005	0.05964003	0.0065625
1.6 MVA 10/0.4 kV DOTE 1600/10 SGB	Three Phase Transformer	1.6	50	10	0.4	6	17	1.0625	5.557812	0.05905175	0.010625	Y	ZN	0	5	Yzn5	6	1.0625	5.557812	0.05905175	0.010625
1.6 MVA 10/0.4 kV DOTEL 1600/10 SGB	Three Phase Transformer	1.6	50	10	0.4	6	17	1.0625	5.557812	0.05905175	0.010625	Y	ZN	0	5	Yzn5	6	1.0625	5.557812	0.05905175	0.010625
1.6 MVA 10/0.4 kV DT 1600/10 F SGB	Three Phase Transformer	1.6	50	10	0.4	6	12.5	0.78125	7.614617	0.0594892	0.0078125	Y	ZN	0	5	Yzn5	6	0.78125	7.614617	0.0594892	0.0078125
1.6 MVA 10/0.4 kV DTKa SGB	Three Phase Transformer	1.6	50	10	0.4	6	13	0.8125	7.316594	0.05944732	0.008125	Y	ZN	0	5	Yzn5	6	0.8125	7.316594	0.05944732	0.008125
1.6 MVA 10/0.4 kV DTTH SGB	Three Phase Transformer	1.6	50	10	0.4	6	12.5	0.78125	7.614617	0.0594892	0.0078125	D	YN	0	5	Dyn5	6	0.78125	7.614617	0.0594892	0.0078125
1.6 MVA 10/0.4 kV DTTHIL SGB	Three Phase Transformer	1.6	50	10	0.4	6	8.8	0.55	10.86316	0.05974738	0.0055	D	YN	0	5	Dyn5	6	0.55	10.86316	0.05974738	0.0055
1.6 MVA 10/0.4 kV DTTHL SGB	Three Phase Transformer	1.6	50	10	0.4	6	11.8	0.7375	8.0739	0.05954502	0.007375	D	YN	0	5	Dyn5	6	0.7375	8.0739	0.05954502	0.007375
1.6 MVA 10/0.4 kV Dyn1 ASEA	Three Phase Transformer	1.6	50	10	0.4	6	12.7	0.7937499	7.492618	0.05947265	0.0079375	D	YN	0	1	Dyn1	6	0.79375	7.492617	0.05947265	0.0079375
1.6 MVA 10/0.4 kV Dyn1 wnr ASEA	Three Phase Transformer	1.6	50	10	0.4	6	12.7	0.7937499	7.492618	0.05947265	0.0079375	D	YN	0	1	Dyn1	6	0.79375	7.492617	0.05947265	0.0079375
1.6 MVA 10/0.4 kV Dyn11 ASEA	Three Phase Transformer	1.6	50	10	0.4	6	12.7	0.7937499	7.492618	0.05947265	0.0079375	D	YN	0	11	Dyn11	6	0.79375	7.492617	0.05947265	0.0079375
1.6 MVA 10/0.4 kV Dyn11 wnr ASEA	Three Phase Transformer	1.6	50	10	0.4	6	12.7	0.7937499	7.492618	0.05947265	0.0079375	D	YN	0	11	Dyn11	6	0.79375	7.492617	0.05947265	0.0079375
1.6 MVA 10/0.4 kV Dyn5 ASEA	Three Phase Transformer	1.6	50	10	0.4	6	12.7	0.7937499	7.492618	0.05947265	0.0079375	D	YN	0	5	Dyn5	6	0.79375	7.492617	0.05947265	0.0079375
1.6 MVA 10/0.4 kV Dyn5 wnr ASEA	Three Phase Transformer	1.6	50	10	0.4	6	12.7	0.7937499	7.492618	0.05947265	0.0079375	D	YN	0	5	Dyn5	6	0.79375	7.492617	0.05947265	0.0079375
1.6 MVA 10/0.4 kV Dyn7 ASEA	Three Phase Transformer	1.6	50	10	0.4	6	12.7	0.7937499	7.492618	0.05947265	0.0079375	D	YN	0	7	Dyn7	6	0.79375	7.492617	0.05947265	0.0079375
1.6 MVA 10/0.4 kV Dyn7 wnr ASEA	Three Phase Transformer	1.6	50	10	0.4	6	12.7	0.7937499	7.492618	0.05947265	0.0079375	D	YN	0	7	Dyn7	6	0.79375	7.492617	0.05947265	0.0079375
1.6 MVA 10/0.4 kV Trafo Union	Three Phase Transformer	1.6	50	10	0.4	6	12.5	0.78125	7.614617	0.0594892	0.0078125	D	YN	0	5	Dyn5	6	0.78125	7.614617	0.0594892	0.0078125
1.6 MVA 10/0.4 kV Trafo Union wnr	Three Phase Transformer	1.6	50	10	0.4	6	13	0.8125	7.316594	0.05944732	0.008125	D	YN	0	5	Dyn5	6	0.8125	7.316594	0.05944732	0.008125
1.6 MVA 10/0.4 kV Yyn0 ASEA	Three Phase Transformer	1.6	50	10	0.4	6	12.7	0.7937499	7.492618	0.05947265	0.0079375	Y	YN	0	0	Yyn0	6	0.79375	7.492617	0.05947265	0.0079375
1.6 MVA 10/0.4 kV Yyn0 wnr ASEA	Three Phase Transformer	1.6	50	10	0.4	6	12.7	0.7937499	7.492618	0.05947265	0.0079375	Y	YN	0	0	Yyn0	6	0.79375	7.492617	0.05947265	0.0079375
1.6 MVA 10/0.4 kV Yyn6 ASEA	Three Phase Transformer	1.6	50	10	0.4	6	12.7	0.7937499	7.492618	0.05947265	0.0079375	Y	YN	0	6	Yyn6	6	0.79375	7.492617	0.05947265	0.0079375
1.6 MVA 10/0.4 kV Yyn6 wnr ASEA	Three Phase Transformer	1.6	50	10	0.4	6	12.7	0.7937499	7.492618	0.05947265	0.0079375	Y	YN	0	6	Yyn6	6	0.79375	7.492617	0.05947265	0.0079375
2 MVA 10/0.4 kV 2.8 GEAFOL	Three Phase Transformer	2	50	10	0.4	6	13	0.65	9.176442	0.05964687	0.0065	D	YN	0	5	Dyn5	6	0.65	9.176443	0.05964687	0.0065
2 MVA 10/0.4 kV 3.9 GEAFOL	Three Phase Transformer	2	50	10	0.4	6	12.7	0.635	9.395753	0.05966303	0.00635	D	YN	0	5	Dyn5	6	0.635	9.395753	0.05966303	0.00635
2 MVA 10/0.4 kV DOTE 2000/10 SGB	Three Phase Transformer	2	50	10	0.4	6	21.5	1.075	5.491081	0.05902912	0.01075	Y	ZN	0	5	Yzn5	6	1.075	5.491081	0.05902912	0.01075
2 MVA 10/0.4 kV DOTEL 2000/10 SGB	Three Phase Transformer	2	50	10	0.4	6	21.5	1.075	5.491081	0.05902912	0.01075	Y	ZN	0	5	Yzn5	6	1.075	5.491081	0.05902912	0.01075
2 MVA 10/0.4 kV DTTH SGB	Three Phase Transformer	2	50	10	0.4	6	16.7	0.8350001	7.115705	0.05941614	0.00835	D	YN	0	5	Dyn5	6	0.835	7.115705	0.05941614	0.00835
2 MVA 10/0.4 kV DTTHIL SGB	Three Phase Transformer	2	50	10	0.4	6	12	0.6	9.949874	0.05969924	0.006	D	YN	0	5	Dyn5	6	0.6	9.949874	0.05969924	0.006
2 MVA 10/0.4 kV DTTHL SGB	Three Phase Transformer	2	50	10	0.4	6	15.3	0.765	7.779126	0.05951031	0.00765	D	YN	0	5	Dyn5	6	0.765	7.779126	0.05951031	0.00765
2 MVA 10/0.4 kV Dyn1 ASEA	Three Phase Transformer	2	50	10	0.4	6	15.5	0.775	7.67708	0.05949737	0.00775	D	YN	0	1	Dyn1	6	0.775	7.67708	0.05949737	0.00775
2 MVA 10/0.4 kV Dyn1 wnr ASEA	Three Phase Transformer	2	50	10	0.4	6	15.5	0.775	7.67708	0.05949737	0.00775	D	YN	0	1	Dyn1	6	0.775	7.67708	0.05949737	0.00775
2 MVA 10/0.4 kV Dyn11 ASEA	Three Phase Transformer	2	50	10	0.4	6	15.5	0.775	7.67708	0.05949737	0.00775	D	YN	0	11	Dyn11	6	0.775	7.67708	0.05949737	0.00775
2 MVA 10/0.4 kV Dyn11 wnr ASEA	Three Phase Transformer	2	50	10	0.4	6	15.5	0.775	7.67708	0.05949737	0.00775	D	YN	0	11	Dyn11	6	0.775	7.67708	0.05949737	0.00775
2 MVA 10/0.4 kV Dyn5 ASEA	Three Phase Transformer	2	50	10	0.4	6	15.5	0.775	7.67708	0.05949737	0.00775	D	YN	0	5	Dyn5	6	0.775	7.67708	0.05949737	0.00775
2 MVA 10/0.4 kV Dyn5 wnr ASEA	Three Phase Transformer	2	50	10	0.4	6	15.5	0.775	7.67708	0.05949737	0.00775	D	YN	0	5	Dyn5	6	0.775	7.67708	0.05949737	0.00775
2 MVA 10/0.4 kV Dyn7 ASEA	Three Phase Transformer	2	50	10	0.4	6	15.5	0.775	7.67708	0.05949737	0.00775	D	YN	0	7	Dyn7	6	0.775	7.67708	0.05949737	0.00775
2 MVA 10/0.4 kV Dyn7 wnr ASEA	Three Phase Transformer	2	50	10	0.4	6	15.5	0.775	7.67708	0.05949737	0.00775	D	YN	0	7	Dyn7	6	0.775	7.67708	0.05949737	0.00775
2 MVA 10/0.4 kV Trafo Union	Three Phase Transformer	2	50	10	0.4	8	15	0.75	10.61969	0.07964766	0.0075	D	YN	0	5	Dyn5	8	0.75	10.61969	0.07964766	0.0075
2 MVA 10/0.4 kV Trafo Union wnr	Three Phase Transformer	2	50	10	0.4	8	15.5	0.775	10.27403	0.07962372	0.00775	D	YN	0	5	Dyn5	8	0.775	10.27403	0.07962372	0.00775
2 MVA 10/0.4 kV Yyn0 ASEA	Three Phase Transformer	2	50	10	0.4	6	15.5	0.775	7.67708	0.05949737	0.00775	Y	YN	0	0	Yyn0	6	0.775	7.67708	0.05949737	0.00775
2 MVA 10/0.4 kV Yyn0 wnr ASEA	Three Phase Transformer	2	50	10	0.4	6	15.5	0.775	7.67708	0.05949737	0.00775	Y	YN	0	0	Yyn0	6	0.775	7.67708	0.05949737	0.00775
2 MVA 10/0.4 kV Yyn6 ASEA	Three Phase Transformer	2	50	10	0.4	6	15.5	0.775	7.67708	0.05949737	0.00775	Y	YN	0	6	Yyn6	6	0.775	7.67708	0.05949737	0.00775
2 MVA 10/0.4 kV Yyn6 wnr ASEA	Three Phase Transformer	2	50	10	0.4	6	15.5	0.775	7.67708	0.05949737	0.00775	Y	YN	0	6	Yyn6	6	0.775	7.67708	0.05949737	0.00775
2.5 MVA 10/0.4 kV 3.3 GEAFOL	Three Phase Transformer	2.5	50	10	0.4	6	19	0.76	7.831147	0.05951672	0.0076	D	YN	0	5	Dyn5	6	0.76	7.831147	0.05951672	0.0076
2.5 MVA 10/0.4 kV 4.8 GEAFOL	Three Phase Transformer	2.5	50	10	0.4	6	15.5	0.62	9.625613	0.0596788	0.0062	D	YN	0	5	Dyn5	6	0.62	9.625613	0.0596788	0.0062
2.5 MVA 10/0.4 kV DOTE 2500/10 SGB	Three Phase Transformer	2.5	50	10	0.4	6	25	1	5.91608	0.0591608	0.01	Y	ZN	0	5	Yzn5	6	1	5.91608	0.0591608	0.01
2.5 MVA 10/0.4 kV DOTEL 2500/10 SGB	Three Phase Transformer	2.5	50	10	0.4	6	25	1	5.91608	0.0591608	0.01	Y	ZN	0	5	Yzn5	6	1	5.91608	0.0591608	0.01
2.5 MVA 10/0.4 kV DTTH SGB	Three Phase Transformer	2.5	50	10	0.4	6	18.5	0.74	8.046205	0.05954191	0.0074	D	YN	0	5	Dyn5	6	0.74	8.046205	0.05954191	0.0074
2.5 MVA 10/0.4 kV DTTHIL SGB	Three Phase Transformer	2.5	50	10	0.4	6	13.9	0.556	10.74493	0.05974183	0.00556	D	YN	0	5	Dyn5	6	0.556	10.74493	0.05974183	0.00556
2.5 MVA 10/0.4 kV DTTHL SGB	Three Phase Transformer	2.5	50	10	0.4	6	18	0.72	8.273115	0.05956643	0.0072	D	YN	0	5	Dyn5	6	0.72	8.273115	0.05956643	0.0072
2.5 MVA 10/0.4 kV Dyn1 ASEA	Three Phase Transformer	2.5	50	10	0.4	6	19	0.76	7.831147	0.05951672	0.0076	D	YN	0	1	Dyn1	6	0.76	7.831147	0.05951672	0.0076
2.5 MVA 10/0.4 kV Dyn1 wnr ASEA	Three Phase Transformer	2.5	50	10	0.4	6	19	0.76	7.831147	0.05951672	0.0076	D	YN	0	1	Dyn1	6	0.76	7.831147	0.05951672	0.0076
2.5 MVA 10/0.4 kV Dyn11 ASEA	Three Phase Transformer	2.5	50	10	0.4	6	19	0.76	7.831147	0.05951672	0.0076	D	YN	0	11	Dyn11	6	0.76	7.831147	0.05951672	0.0076
2.5 MVA 10/0.4 kV Dyn11 wnr ASEA	Three Phase Transformer	2.5	50	10	0.4	6	19	0.76	7.831147	0.05951672	0.0076	D	YN	0	11	Dyn11	6	0.76	7.831147	0.05951672	0.0076
2.5 MVA 10/0.4 kV Dyn5 ASEA	Three Phase Transformer	2.5	50	10	0.4	6	19	0.76	7.831147	0.05951672	0.0076	D	YN	0	5	Dyn5	6	0.76	7.831147	0.05951672	0.0076
2.5 MVA 10/0.4 kV Dyn5 wnr ASEA	Three Phase Transformer	2.5	50	10	0.4	6	19	0.76	7.831147	0.05951672	0.0076	D	YN	0	5	Dyn5	6	0.76	7.831147	0.05951672	0.0076
2.5 MVA 10/0.4 kV Dyn7 ASEA	Three Phase Transformer	2.5	50	10	0.4	6	19	0.76	7.831147	0.05951672	0.0076	D	YN	0	7	Dyn7	6	0.76	7.831147	0.05951672	0.0076
2.5 MVA 10/0.4 kV Dyn7 wnr ASEA	Three Phase Transformer	2.5	50	10	0.4	6	19	0.76	7.831147	0.05951672	0.0076	D	YN	0	7	Dyn7	6	0.76	7.831147	0.05951672	0.0076
2.5 MVA 10/0.4 kV Trafo Union	Three Phase Transformer	2.5	50	10	0.4	8	17.5	0.7	11.38474	0.07969316	0.007	D	YN	0	5	Dyn5	8	0.7	11.38474	0.07969316	0.007
2.5 MVA 10/0.4 kV Trafo Union wnr	Three Phase Transformer	2.5	50	10	0.4	8	18	0.72	11.06602	0.07967534	0.0072	D	YN	0	5	Dyn5	8	0.72	11.06602	0.07967534	0.0072
2.5 MVA 10/0.4 kV Yyn0 ASEA	Three Phase Transformer	2.5	50	10	0.4	6	19	0.76	7.831147	0.05951672	0.0076	Y	YN	0	0	Yyn0	6	0.76	7.831147	0.05951672	0.0076
2.5 MVA 10/0.4 kV Yyn0 wnr ASEA	Three Phase Transformer	2.5	50	10	0.4	6	19	0.76	7.831147	0.05951672	0.0076	Y	YN	0	0	Yyn0	6	0.76	7.831147	0.05951672	0.0076
2.5 MVA 10/0.4 kV Yyn6 ASEA	Three Phase Transformer	2.5	50	10	0.4	6	19	0.76	7.831147	0.05951672	0.0076	Y	YN	0	6	Yyn6	6	0.76	7.831147	0.05951672	0.0076
2.5 MVA 10/0.4 kV Yyn6 wnr ASEA	Three Phase Transformer	2.5	50	10	0.4	6	19	0.76	7.831147	0.05951672	0.0076	Y	YN	0	6	Yyn6	6	0.76	7.831147	0.05951672	0.0076
0.25 MVA 20/0.4 kV Dyn0 wnr 60 ASEA	Three Phase Transformer	0.25	60	20	0.4	7.05	3.3	1.32	5.246457	0.06925323	0.0132	D	YN	0	0	Dyn0	7.05	1.32	5.246456	0.06925323	0.0132
0.25 MVA 20/0.4 kV Dyn1 60 ASEA	Three Phase Transformer	0.25	60	20	0.4	7.05	3.3	1.32	5.246457	0.06925323	0.0132	D	YN	0	1	Dyn1	7.05	1.32	5.246456	0.06925323	0.0132
0.25 MVA 20/0.4 kV Dyn1 wnr 60 ASEA	Three Phase Transformer	0.25	60	20	0.4	7.05	3.3	1.32	5.246457	0.06925323	0.0132	D	YN	0	1	Dyn1	7.05	1.32	5.246456	0.06925323	0.0132
0.25 MVA 20/0.4 kV Dyn11 60 ASEA	Three Phase Transformer	0.25	60	20	0.4	7.05	3.3	1.32	5.246457	0.06925323	0.0132	D	YN	0	11	Dyn11	7.05	1.32	5.246456	0.06925323	0.0132
0.25 MVA 20/0.4 kV Dyn11 wnr 60 ASEA	Three Phase Transformer	0.25	60	20	0.4	7.05	3.3	1.32	5.246457	0.06925323	0.0132	D	YN	0	11	Dyn11	7.05	1.32	5.246456	0.06925323	0.0132
0.25 MVA 20/0.4 kV Dyn5 60 ASEA	Three Phase Transformer	0.25	60	20	0.4	7.05	3.3	1.32	5.246457	0.06925323	0.0132	D	YN	0	5	Dyn5	7.05	1.32	5.246456	0.06925323	0.0132
0.25 MVA 20/0.4 kV Dyn7 60 ASEA	Three Phase Transformer	0.25	60	20	0.4	7.05	3.3	1.32	5.246457	0.06925323	0.0132	D	YN	0	7	Dyn7	7.05	1.32	5.246456	0.06925323	0.0132
0.25 MVA 20/0.4 kV Dyn7 wnr 60 ASEA	Three Phase Transformer	0.25	60	20	0.4	7.05	3.3	1.32	5.246457	0.06925323	0.0132	D	YN	0	7	Dyn7	7.05	1.32	5.246456	0.06925323	0.0132
0.25 MVA 20/0.4 kV Yyn0 60 ASEA	Three Phase Transformer	0.25	60	20	0.4	7.05	3.3	1.32	5.246457	0.06925323	0.0132	Y	YN	0	0	Yyn0	7.05	1.32	5.246456	0.06925323	0.0132
0.25 MVA 20/0.4 kV Yyn0 wnr 60 ASEA	Three Phase Transformer	0.25	60	20	0.4	7.05	3.3	1.32	5.246457	0.06925323	0.0132	Y	YN	0	0	Yyn0	7.05	1.32	5.246456	0.06925323	0.0132
0.25 MVA 20/0.4 kV Yyn6 60 ASEA	Three Phase Transformer	0.25	60	20	0.4	7.05	3.3	1.32	5.246457	0.06925323	0.0132	Y	YN	0	6	Yyn6	7.05	1.32	5.246456	0.06925323	0.0132
0.25 MVA 20/0.4 kV Yyn6 wnr 60 ASEA	Three Phase Transformer	0.25	60	20	0.4	7.05	3.3	1.32	5.246457	0.06925323	0.0132	Y	YN	0	6	Yyn6	7.05	1.32	5.246456	0.06925323	0.0132
0.315 MVA 20/0.4 kV Dyn0 wnr 60 ASEA	Three Phase Transformer	0.315	60	20	0.4	7.05	4	1.269841	5.461073	0.06934696	0.01269841	D	YN	0	0	Dyn0	7.05	1.269841	5.461074	0.06934696	0.01269841
0.315 MVA 20/0.4 kV Dyn1 60 ASEA	Three Phase Transformer	0.315	60	20	0.4	7.05	4	1.269841	5.461073	0.06934696	0.01269841	D	YN	0	1	Dyn1	7.05	1.269841	5.461074	0.06934696	0.01269841
0.315 MVA 20/0.4 kV Dyn1 wnr 60 ASEA	Three Phase Transformer	0.315	60	20	0.4	7.05	4	1.269841	5.461073	0.06934696	0.01269841	D	YN	0	1	Dyn1	7.05	1.269841	5.461074	0.06934696	0.01269841
0.315 MVA 20/0.4 kV Dyn11 60 ASEA	Three Phase Transformer	0.315	60	20	0.4	7.05	4	1.269841	5.461073	0.06934696	0.01269841	D	YN	0	11	Dyn11	7.05	1.269841	5.461074	0.06934696	0.01269841
0.315 MVA 20/0.4 kV Dyn11 wnr 60 ASEA	Three Phase Transformer	0.315	60	20	0.4	7.05	4	1.269841	5.461073	0.06934696	0.01269841	D	YN	0	11	Dyn11	7.05	1.269841	5.461074	0.06934696	0.01269841
0.315 MVA 20/0.4 kV Dyn5 60 ASEA	Three Phase Transformer	0.315	60	20	0.4	7.05	4	1.269841	5.461073	0.06934696	0.01269841	D	YN	0	5	Dyn5	7.05	1.269841	5.461074	0.06934696	0.01269841
0.315 MVA 20/0.4 kV Dyn7 60 ASEA	Three Phase Transformer	0.315	60	20	0.4	7.05	4	1.269841	5.461073	0.06934696	0.01269841	D	YN	0	7	Dyn7	7.05	1.269841	5.461074	0.06934696	0.01269841
0.315 MVA 20/0.4 kV Dyn7 wnr 60 ASEA	Three Phase Transformer	0.315	60	20	0.4	7.05	4	1.269841	5.461073	0.06934696	0.01269841	D	YN	0	7	Dyn7	7.05	1.269841	5.461074	0.06934696	0.01269841
0.315 MVA 20/0.4 kV Yyn0 60 ASEA	Three Phase Transformer	0.315	60	20	0.4	7.05	4	1.269841	5.461073	0.06934696	0.01269841	Y	YN	0	0	Yyn0	7.05	1.269841	5.461074	0.06934696	0.01269841
0.315 MVA 20/0.4 kV Yyn0 wnr 60 ASEA	Three Phase Transformer	0.315	60	20	0.4	7.05	4	1.269841	5.461073	0.06934696	0.01269841	Y	YN	0	0	Yyn0	7.05	1.269841	5.461074	0.06934696	0.01269841
0.315 MVA 20/0.4 kV Yyn6 60 ASEA	Three Phase Transformer	0.315	60	20	0.4	7.05	4	1.269841	5.461073	0.06934696	0.01269841	Y	YN	0	6	Yyn6	7.05	1.269841	5.461074	0.06934696	0.01269841
0.315 MVA 20/0.4 kV Yyn6 wnr 60 ASEA	Three Phase Transformer	0.315	60	20	0.4	7.05	4	1.269841	5.461073	0.06934696	0.01269841	Y	YN	0	6	Yyn6	7.05	1.269841	5.461074	0.06934696	0.01269841
0.4 MVA 20/0.4 kV Dyn0 wnr 60 ASEA	Three Phase Transformer	0.4	60	20	0.4	7.05	4.8	1.2	5.789268	0.06947122	0.012	D	YN	0	0	Dyn0	7.05	1.2	5.789268	0.06947122	0.012
0.4 MVA 20/0.4 kV Dyn1 60 ASEA	Three Phase Transformer	0.4	60	20	0.4	7.05	4.8	1.2	5.789268	0.06947122	0.012	D	YN	0	1	Dyn1	7.05	1.2	5.789268	0.06947122	0.012
0.4 MVA 20/0.4 kV Dyn1 wnr 60 ASEA	Three Phase Transformer	0.4	60	20	0.4	7.05	4.8	1.2	5.789268	0.06947122	0.012	D	YN	0	1	Dyn1	7.05	1.2	5.789268	0.06947122	0.012
0.4 MVA 20/0.4 kV Dyn11 60 ASEA	Three Phase Transformer	0.4	60	20	0.4	7.05	4.8	1.2	5.789268	0.06947122	0.012	D	YN	0	11	Dyn11	7.05	1.2	5.789268	0.06947122	0.012
0.4 MVA 20/0.4 kV Dyn11 wnr 60 ASEA	Three Phase Transformer	0.4	60	20	0.4	7.05	4.8	1.2	5.789268	0.06947122	0.012	D	YN	0	11	Dyn11	7.05	1.2	5.789268	0.06947122	0.012
0.4 MVA 20/0.4 kV Dyn5 60 ASEA	Three Phase Transformer	0.4	60	20	0.4	7.05	4.8	1.2	5.789268	0.06947122	0.012	D	YN	0	5	Dyn5	7.05	1.2	5.789268	0.06947122	0.012
0.4 MVA 20/0.4 kV Dyn7 60 ASEA	Three Phase Transformer	0.4	60	20	0.4	7.05	4.8	1.2	5.789268	0.06947122	0.012	D	YN	0	7	Dyn7	7.05	1.2	5.789268	0.06947122	0.012
0.4 MVA 20/0.4 kV Dyn7 wnr 60 ASEA	Three Phase Transformer	0.4	60	20	0.4	7.05	4.8	1.2	5.789268	0.06947122	0.012	D	YN	0	7	Dyn7	7.05	1.2	5.789268	0.06947122	0.012
0.4 MVA 20/0.4 kV Yyn0 60 ASEA	Three Phase Transformer	0.4	60	20	0.4	7.05	4.8	1.2	5.789268	0.06947122	0.012	Y	YN	0	0	Yyn0	7.05	1.2	5.789268	0.06947122	0.012
0.4 MVA 20/0.4 kV Yyn0 wnr 60 ASEA	Three Phase Transformer	0.4	60	20	0.4	7.05	4.8	1.2	5.789268	0.06947122	0.012	Y	YN	0	0	Yyn0	7.05	1.2	5.789268	0.06947122	0.012
0.4 MVA 20/0.4 kV Yyn6 60 ASEA	Three Phase Transformer	0.4	60	20	0.4	7.05	4.8	1.2	5.789268	0.06947122	0.012	Y	YN	0	6	Yyn6	7.05	1.2	5.789268	0.06947122	0.012
0.4 MVA 20/0.4 kV Yyn6 wnr 60 ASEA	Three Phase Transformer	0.4	60	20	0.4	7.05	4.8	1.2	5.789268	0.06947122	0.012	Y	YN	0	6	Yyn6	7.05	1.2	5.789268	0.06947122	0.012
0.5 MVA 20/0.4 kV Dyn0 wnr 60 ASEA	Three Phase Transformer	0.5	60	20	0.4	7.05	6	1.2	5.789268	0.06947122	0.012	D	YN	0	0	Dyn0	7.05	1.2	5.789268	0.06947122	0.012
0.5 MVA 20/0.4 kV Dyn1 60 ASEA	Three Phase Transformer	0.5	60	20	0.4	7.05	6	1.2	5.789268	0.06947122	0.012	D	YN	0	1	Dyn1	7.05	1.2	5.789268	0.06947122	0.012
0.5 MVA 20/0.4 kV Dyn1 wnr 60 ASEA	Three Phase Transformer	0.5	60	20	0.4	7.05	6	1.2	5.789268	0.06947122	0.012	D	YN	0	1	Dyn1	7.05	1.2	5.789268	0.06947122	0.012
0.5 MVA 20/0.4 kV Dyn11 60 ASEA	Three Phase Transformer	0.5	60	20	0.4	7.05	6	1.2	5.789268	0.06947122	0.012	D	YN	0	11	Dyn11	7.05	1.2	5.789268	0.06947122	0.012
0.5 MVA 20/0.4 kV Dyn11 wnr 60 ASEA	Three Phase Transformer	0.5	60	20	0.4	7.05	6	1.2	5.789268	0.06947122	0.012	D	YN	0	11	Dyn11	7.05	1.2	5.789268	0.06947122	0.012
0.5 MVA 20/0.4 kV Dyn5 60 ASEA	Three Phase Transformer	0.5	60	20	0.4	7.05	6	1.2	5.789268	0.06947122	0.012	D	YN	0	5	Dyn5	7.05	1.2	5.789268	0.06947122	0.012
0.5 MVA 20/0.4 kV Dyn7 60 ASEA	Three Phase Transformer	0.5	60	20	0.4	7.05	6	1.2	5.789268	0.06947122	0.012	D	YN	0	7	Dyn7	7.05	1.2	5.789268	0.06947122	0.012
0.5 MVA 20/0.4 kV Dyn7 wnr 60 ASEA	Three Phase Transformer	0.5	60	20	0.4	7.05	6	1.2	5.789268	0.06947122	0.012	D	YN	0	7	Dyn7	7.05	1.2	5.789268	0.06947122	0.012
0.5 MVA 20/0.4 kV Yyn0 60 ASEA	Three Phase Transformer	0.5	60	20	0.4	7.05	6	1.2	5.789268	0.06947122	0.012	Y	YN	0	0	Yyn0	7.05	1.2	5.789268	0.06947122	0.012
0.5 MVA 20/0.4 kV Yyn0 wnr 60 ASEA	Three Phase Transformer	0.5	60	20	0.4	7.05	6	1.2	5.789268	0.06947122	0.012	Y	YN	0	0	Yyn0	7.05	1.2	5.789268	0.06947122	0.012
0.5 MVA 20/0.4 kV Yyn6 60 ASEA	Three Phase Transformer	0.5	60	20	0.4	7.05	6	1.2	5.789268	0.06947122	0.012	Y	YN	0	6	Yyn6	7.05	1.2	5.789268	0.06947122	0.012
0.5 MVA 20/0.4 kV Yyn6 wnr 60 ASEA	Three Phase Transformer	0.5	60	20	0.4	7.05	6	1.2	5.789268	0.06947122	0.012	Y	YN	0	6	Yyn6	7.05	1.2	5.789268	0.06947122	0.012
0.63 MVA 20/0.4 kV Dyn0 wnr 60 ASEA	Three Phase Transformer	0.63	60	20	0.4	7.05	6.9	1.095238	6.358806	0.06964406	0.01095238	D	YN	0	0	Dyn0	7.05	1.095238	6.358807	0.06964406	0.01095238
0.63 MVA 20/0.4 kV Dyn1 60 ASEA	Three Phase Transformer	0.63	60	20	0.4	7.05	6.9	1.095238	6.358806	0.06964406	0.01095238	D	YN	0	1	Dyn1	7.05	1.095238	6.358807	0.06964406	0.01095238
0.63 MVA 20/0.4 kV Dyn1 wnr 60 ASEA	Three Phase Transformer	0.63	60	20	0.4	7.05	6.9	1.095238	6.358806	0.06964406	0.01095238	D	YN	0	1	Dyn1	7.05	1.095238	6.358807	0.06964406	0.01095238
0.63 MVA 20/0.4 kV Dyn11 60 ASEA	Three Phase Transformer	0.63	60	20	0.4	7.05	6.9	1.095238	6.358806	0.06964406	0.01095238	D	YN	0	11	Dyn11	7.05	1.095238	6.358807	0.06964406	0.01095238
0.63 MVA 20/0.4 kV Dyn11 wnr 60 ASEA	Three Phase Transformer	0.63	60	20	0.4	7.05	6.9	1.095238	6.358806	0.06964406	0.01095238	D	YN	0	11	Dyn11	7.05	1.095238	6.358807	0.06964406	0.01095238
0.63 MVA 20/0.4 kV Dyn5 60 ASEA	Three Phase Transformer	0.63	60	20	0.4	7.05	6.9	1.095238	6.358806	0.06964406	0.01095238	D	YN	0	5	Dyn5	7.05	1.095238	6.358807	0.06964406	0.01095238
0.63 MVA 20/0.4 kV Dyn7 60 ASEA	Three Phase Transformer	0.63	60	20	0.4	7.05	6.9	1.095238	6.358806	0.06964406	0.01095238	D	YN	0	7	Dyn7	7.05	1.095238	6.358807	0.06964406	0.01095238
0.63 MVA 20/0.4 kV Dyn7 wnr 60 ASEA	Three Phase Transformer	0.63	60	20	0.4	7.05	6.9	1.095238	6.358806	0.06964406	0.01095238	D	YN	0	7	Dyn7	7.05	1.095238	6.358807	0.06964406	0.01095238
0.63 MVA 20/0.4 kV Yyn0 60 ASEA	Three Phase Transformer	0.63	60	20	0.4	7.05	6.9	1.095238	6.358806	0.06964406	0.01095238	Y	YN	0	0	Yyn0	7.05	1.095238	6.358807	0.06964406	0.01095238
0.63 MVA 20/0.4 kV Yyn0 wnr 60 ASEA	Three Phase Transformer	0.63	60	20	0.4	7.05	6.9	1.095238	6.358806	0.06964406	0.01095238	Y	YN	0	0	Yyn0	7.05	1.095238	6.358807	0.06964406	0.01095238
0.63 MVA 20/0.4 kV Yyn6 60 ASEA	Three Phase Transformer	0.63	60	20	0.4	7.05	6.9	1.095238	6.358806	0.06964406	0.01095238	Y	YN	0	6	Yyn6	7.05	1.095238	6.358807	0.06964406	0.01095238
0.63 MVA 20/0.4 kV Yyn6 wnr 60 ASEA	Three Phase Transformer	0.63	60	20	0.4	7.05	6.9	1.095238	6.358806	0.06964406	0.01095238	Y	YN	0	6	Yyn6	7.05	1.095238	6.358807	0.06964406	0.01095238
0.8 MVA 20/0.4 kV Dyn0 wnr 60 ASEA	Three Phase Transformer	0.8	60	20	0.4	7.05	8.1	1.0125	6.89078	0.06976915	0.010125	D	YN	0	0	Dyn0	7.05	1.0125	6.89078	0.06976915	0.010125
0.8 MVA 20/0.4 kV Dyn1 60 ASEA	Three Phase Transformer	0.8	60	20	0.4	7.05	8.1	1.0125	6.89078	0.06976915	0.010125	D	YN	0	1	Dyn1	7.05	1.0125	6.89078	0.06976915	0.010125
0.8 MVA 20/0.4 kV Dyn1 wnr 60 ASEA	Three Phase Transformer	0.8	60	20	0.4	7.05	8.1	1.0125	6.89078	0.06976915	0.010125	D	YN	0	1	Dyn1	7.05	1.0125	6.89078	0.06976915	0.010125
0.8 MVA 20/0.4 kV Dyn11 60 ASEA	Three Phase Transformer	0.8	60	20	0.4	7.05	8.1	1.0125	6.89078	0.06976915	0.010125	D	YN	0	11	Dyn11	7.05	1.0125	6.89078	0.06976915	0.010125
0.8 MVA 20/0.4 kV Dyn11 wnr 60 ASEA	Three Phase Transformer	0.8	60	20	0.4	7.05	8.1	1.0125	6.89078	0.06976915	0.010125	D	YN	0	11	Dyn11	7.05	1.0125	6.89078	0.06976915	0.010125
0.8 MVA 20/0.4 kV Dyn5 60 ASEA	Three Phase Transformer	0.8	60	20	0.4	7.05	8.1	1.0125	6.89078	0.06976915	0.010125	D	YN	0	5	Dyn5	7.05	1.0125	6.89078	0.06976915	0.010125
0.8 MVA 20/0.4 kV Dyn7 60 ASEA	Three Phase Transformer	0.8	60	20	0.4	7.05	8.1	1.0125	6.89078	0.06976915	0.010125	D	YN	0	7	Dyn7	7.05	1.0125	6.89078	0.06976915	0.010125
0.8 MVA 20/0.4 kV Dyn7 wnr 60 ASEA	Three Phase Transformer	0.8	60	20	0.4	7.05	8.1	1.0125	6.89078	0.06976915	0.010125	D	YN	0	7	Dyn7	7.05	1.0125	6.89078	0.06976915	0.010125
0.8 MVA 20/0.4 kV Yyn0 60 ASEA	Three Phase Transformer	0.8	60	20	0.4	7.05	8.1	1.0125	6.89078	0.06976915	0.010125	Y	YN	0	0	Yyn0	7.05	1.0125	6.89078	0.06976915	0.010125
0.8 MVA 20/0.4 kV Yyn0 wnr 60 ASEA	Three Phase Transformer	0.8	60	20	0.4	7.05	8.1	1.0125	6.89078	0.06976915	0.010125	Y	YN	0	0	Yyn0	7.05	1.0125	6.89078	0.06976915	0.010125
0.8 MVA 20/0.4 kV Yyn6 60 ASEA	Three Phase Transformer	0.8	60	20	0.4	7.05	8.1	1.0125	6.89078	0.06976915	0.010125	Y	YN	0	6	Yyn6	7.05	1.0125	6.89078	0.06976915	0.010125
0.8 MVA 20/0.4 kV Yyn6 wnr 60 ASEA	Three Phase Transformer	0.8	60	20	0.4	7.05	8.1	1.0125	6.89078	0.06976915	0.010125	Y	YN	0	6	Yyn6	7.05	1.0125	6.89078	0.06976915	0.010125
1 MVA 20/0.4 kV Dyn0 wnr 60 ASEA	Three Phase Transformer	1	60	20	0.4	7.05	9.6	0.96	7.275346	0.06984333	0.0096	D	YN	0	0	Dyn0	7.05	0.96	7.275347	0.06984333	0.0096
1 MVA 20/0.4 kV Dyn1 60 ASEA	Three Phase Transformer	1	60	20	0.4	7.05	9.6	0.96	7.275346	0.06984333	0.0096	D	YN	0	1	Dyn1	7.05	0.96	7.275347	0.06984333	0.0096
1 MVA 20/0.4 kV Dyn1 wnr 60 ASEA	Three Phase Transformer	1	60	20	0.4	7.05	9.6	0.96	7.275346	0.06984333	0.0096	D	YN	0	1	Dyn1	7.05	0.96	7.275347	0.06984333	0.0096
1 MVA 20/0.4 kV Dyn11 60 ASEA	Three Phase Transformer	1	60	20	0.4	7.05	9.6	0.96	7.275346	0.06984333	0.0096	D	YN	0	11	Dyn11	7.05	0.96	7.275347	0.06984333	0.0096
1 MVA 20/0.4 kV Dyn11 wnr 60 ASEA	Three Phase Transformer	1	60	20	0.4	7.05	9.6	0.96	7.275346	0.06984333	0.0096	D	YN	0	11	Dyn11	7.05	0.96	7.275347	0.06984333	0.0096
1 MVA 20/0.4 kV Dyn5 60 ASEA	Three Phase Transformer	1	60	20	0.4	7.05	9.6	0.96	7.275346	0.06984333	0.0096	D	YN	0	5	Dyn5	7.05	0.96	7.275347	0.06984333	0.0096
1 MVA 20/0.4 kV Dyn7 60 ASEA	Three Phase Transformer	1	60	20	0.4	7.05	9.6	0.96	7.275346	0.06984333	0.0096	D	YN	0	7	Dyn7	7.05	0.96	7.275347	0.06984333	0.0096
1 MVA 20/0.4 kV Dyn7 wnr 60 ASEA	Three Phase Transformer	1	60	20	0.4	7.05	9.6	0.96	7.275346	0.06984333	0.0096	D	YN	0	7	Dyn7	7.05	0.96	7.275347	0.06984333	0.0096
1 MVA 20/0.4 kV Yyn0 60 ASEA	Three Phase Transformer	1	60	20	0.4	7.05	9.6	0.96	7.275346	0.06984333	0.0096	Y	YN	0	0	Yyn0	7.05	0.96	7.275347	0.06984333	0.0096
1 MVA 20/0.4 kV Yyn0 wnr 60 ASEA	Three Phase Transformer	1	60	20	0.4	7.05	9.6	0.96	7.275346	0.06984333	0.0096	Y	YN	0	0	Yyn0	7.05	0.96	7.275347	0.06984333	0.0096
1 MVA 20/0.4 kV Yyn6 60 ASEA	Three Phase Transformer	1	60	20	0.4	7.05	9.6	0.96	7.275346	0.06984333	0.0096	Y	YN	0	6	Yyn6	7.05	0.96	7.275347	0.06984333	0.0096
1 MVA 20/0.4 kV Yyn6 wnr 60 ASEA	Three Phase Transformer	1	60	20	0.4	7.05	9.6	0.96	7.275346	0.06984333	0.0096	Y	YN	0	6	Yyn6	7.05	0.96	7.275347	0.06984333	0.0096
1.25 MVA 20/0.4 kV Dyn0 wnr 60 ASEA	Three Phase Transformer	1.25	60	20	0.4	7.05	11.5	0.92	7.597515	0.06989714	0.0092	D	YN	0	0	Dyn0	7.05	0.92	7.597515	0.06989714	0.0092
1.25 MVA 20/0.4 kV Dyn1 60 ASEA	Three Phase Transformer	1.25	60	20	0.4	7.05	11.5	0.92	7.597515	0.06989714	0.0092	D	YN	0	1	Dyn1	7.05	0.92	7.597515	0.06989714	0.0092
1.25 MVA 20/0.4 kV Dyn1 wnr 60 ASEA	Three Phase Transformer	1.25	60	20	0.4	7.05	11.5	0.92	7.597515	0.06989714	0.0092	D	YN	0	1	Dyn1	7.05	0.92	7.597515	0.06989714	0.0092
1.25 MVA 20/0.4 kV Dyn11 60 ASEA	Three Phase Transformer	1.25	60	20	0.4	7.05	11.5	0.92	7.597515	0.06989714	0.0092	D	YN	0	11	Dyn11	7.05	0.92	7.597515	0.06989714	0.0092
1.25 MVA 20/0.4 kV Dyn11 wnr 60 ASEA	Three Phase Transformer	1.25	60	20	0.4	7.05	11.5	0.92	7.597515	0.06989714	0.0092	D	YN	0	11	Dyn11	7.05	0.92	7.597515	0.06989714	0.0092
1.25 MVA 20/0.4 kV Dyn5 60 ASEA	Three Phase Transformer	1.25	60	20	0.4	7.05	11.5	0.92	7.597515	0.06989714	0.0092	D	YN	0	5	Dyn5	7.05	0.92	7.597515	0.06989714	0.0092
1.25 MVA 20/0.4 kV Dyn7 60 ASEA	Three Phase Transformer	1.25	60	20	0.4	7.05	11.5	0.92	7.597515	0.06989714	0.0092	D	YN	0	7	Dyn7	7.05	0.92	7.597515	0.06989714	0.0092
1.25 MVA 20/0.4 kV Dyn7 wnr 60 ASEA	Three Phase Transformer	1.25	60	20	0.4	7.05	11.5	0.92	7.597515	0.06989714	0.0092	D	YN	0	7	Dyn7	7.05	0.92	7.597515	0.06989714	0.0092
1.25 MVA 20/0.4 kV Yyn0 60 ASEA	Three Phase Transformer	1.25	60	20	0.4	7.05	11.5	0.92	7.597515	0.06989714	0.0092	Y	YN	0	0	Yyn0	7.05	0.92	7.597515	0.06989714	0.0092
1.25 MVA 20/0.4 kV Yyn0 wnr 60 ASEA	Three Phase Transformer	1.25	60	20	0.4	7.05	11.5	0.92	7.597515	0.06989714	0.0092	Y	YN	0	0	Yyn0	7.05	0.92	7.597515	0.06989714	0.0092
1.25 MVA 20/0.4 kV Yyn6 60 ASEA	Three Phase Transformer	1.25	60	20	0.4	7.05	11.5	0.92	7.597515	0.06989714	0.0092	Y	YN	0	6	Yyn6	7.05	0.92	7.597515	0.06989714	0.0092
1.25 MVA 20/0.4 kV Yyn6 wnr 60 ASEA	Three Phase Transformer	1.25	60	20	0.4	7.05	11.5	0.92	7.597515	0.06989714	0.0092	Y	YN	0	6	Yyn6	7.05	0.92	7.597515	0.06989714	0.0092
1.6 MVA 20/0.4 kV Dyn0 wnr 60 ASEA	Three Phase Transformer	1.6	60	20	0.4	7.05	14	0.875	7.994845	0.06995489	0.00875	D	YN	0	0	Dyn0	7.05	0.875	7.994845	0.06995489	0.00875
1.6 MVA 20/0.4 kV Dyn1 60 ASEA	Three Phase Transformer	1.6	60	20	0.4	7.05	14	0.875	7.994845	0.06995489	0.00875	D	YN	0	1	Dyn1	7.05	0.875	7.994845	0.06995489	0.00875
1.6 MVA 20/0.4 kV Dyn1 wnr 60 ASEA	Three Phase Transformer	1.6	60	20	0.4	7.05	14	0.875	7.994845	0.06995489	0.00875	D	YN	0	1	Dyn1	7.05	0.875	7.994845	0.06995489	0.00875
1.6 MVA 20/0.4 kV Dyn11 60 ASEA	Three Phase Transformer	1.6	60	20	0.4	7.05	14	0.875	7.994845	0.06995489	0.00875	D	YN	0	11	Dyn11	7.05	0.875	7.994845	0.06995489	0.00875
1.6 MVA 20/0.4 kV Dyn11 wnr 60 ASEA	Three Phase Transformer	1.6	60	20	0.4	7.05	14	0.875	7.994845	0.06995489	0.00875	D	YN	0	11	Dyn11	7.05	0.875	7.994845	0.06995489	0.00875
1.6 MVA 20/0.4 kV Dyn5 60 ASEA	Three Phase Transformer	1.6	60	20	0.4	7.05	14	0.875	7.994845	0.06995489	0.00875	D	YN	0	5	Dyn5	7.05	0.875	7.994845	0.06995489	0.00875
1.6 MVA 20/0.4 kV Dyn7 60 ASEA	Three Phase Transformer	1.6	60	20	0.4	7.05	14	0.875	7.994845	0.06995489	0.00875	D	YN	0	7	Dyn7	7.05	0.875	7.994845	0.06995489	0.00875
1.6 MVA 20/0.4 kV Dyn7 wnr 60 ASEA	Three Phase Transformer	1.6	60	20	0.4	7.05	14	0.875	7.994845	0.06995489	0.00875	D	YN	0	7	Dyn7	7.05	0.875	7.994845	0.06995489	0.00875
1.6 MVA 20/0.4 kV Yyn0 60 ASEA	Three Phase Transformer	1.6	60	20	0.4	7.05	14	0.875	7.994845	0.06995489	0.00875	Y	YN	0	0	Yyn0	7.05	0.875	7.994845	0.06995489	0.00875
1.6 MVA 20/0.4 kV Yyn0 wnr 60 ASEA	Three Phase Transformer	1.6	60	20	0.4	7.05	14	0.875	7.994845	0.06995489	0.00875	Y	YN	0	0	Yyn0	7.05	0.875	7.994845	0.06995489	0.00875
1.6 MVA 20/0.4 kV Yyn6 60 ASEA	Three Phase Transformer	1.6	60	20	0.4	7.05	14	0.875	7.994845	0.06995489	0.00875	Y	YN	0	6	Yyn6	7.05	0.875	7.994845	0.06995489	0.00875
1.6 MVA 20/0.4 kV Yyn6 wnr 60 ASEA	Three Phase Transformer	1.6	60	20	0.4	7.05	14	0.875	7.994845	0.06995489	0.00875	Y	YN	0	6	Yyn6	7.05	0.875	7.994845	0.06995489	0.00875
2 MVA 20/0.4 kV Dyn0 wnr 60 ASEA	Three Phase Transformer	2	60	20	0.4	9.4	16.7	0.8350001	11.21298	0.0936284	0.00835	D	YN	0	0	Dyn0	9.4	0.835	11.21298	0.0936284	0.00835
2 MVA 20/0.4 kV Dyn1 60 ASEA	Three Phase Transformer	2	60	20	0.4	9.4	16.7	0.8350001	11.21298	0.0936284	0.00835	D	YN	0	1	Dyn1	9.4	0.835	11.21298	0.0936284	0.00835
2 MVA 20/0.4 kV Dyn1 wnr 60 ASEA	Three Phase Transformer	2	60	20	0.4	9.4	16.7	0.8350001	11.21298	0.0936284	0.00835	D	YN	0	1	Dyn1	9.4	0.835	11.21298	0.0936284	0.00835
2 MVA 20/0.4 kV Dyn11 60 ASEA	Three Phase Transformer	2	60	20	0.4	9.4	16.7	0.8350001	11.21298	0.0936284	0.00835	D	YN	0	11	Dyn11	9.4	0.835	11.21298	0.0936284	0.00835
2 MVA 20/0.4 kV Dyn11 wnr 60 ASEA	Three Phase Transformer	2	60	20	0.4	9.4	16.7	0.8350001	11.21298	0.0936284	0.00835	D	YN	0	11	Dyn11	9.4	0.835	11.21298	0.0936284	0.00835
2 MVA 20/0.4 kV Dyn5 60 ASEA	Three Phase Transformer	2	60	20	0.4	9.4	16.7	0.8350001	11.21298	0.0936284	0.00835	D	YN	0	5	Dyn5	9.4	0.835	11.21298	0.0936284	0.00835
2 MVA 20/0.4 kV Dyn7 60 ASEA	Three Phase Transformer	2	60	20	0.4	9.4	16.7	0.8350001	11.21298	0.0936284	0.00835	D	YN	0	7	Dyn7	9.4	0.835	11.21298	0.0936284	0.00835
2 MVA 20/0.4 kV Dyn7 wnr 60 ASEA	Three Phase Transformer	2	60	20	0.4	9.4	16.7	0.8350001	11.21298	0.0936284	0.00835	D	YN	0	7	Dyn7	9.4	0.835	11.21298	0.0936284	0.00835
2 MVA 20/0.4 kV Yyn0 60 ASEA	Three Phase Transformer	2	60	20	0.4	9.4	16.7	0.8350001	11.21298	0.0936284	0.00835	Y	YN	0	0	Yyn0	9.4	0.835	11.21298	0.0936284	0.00835
2 MVA 20/0.4 kV Yyn0 wnr 60 ASEA	Three Phase Transformer	2	60	20	0.4	9.4	16.7	0.8350001	11.21298	0.0936284	0.00835	Y	YN	0	0	Yyn0	9.4	0.835	11.21298	0.0936284	0.00835
2 MVA 20/0.4 kV Yyn6 60 ASEA	Three Phase Transformer	2	60	20	0.4	9.4	16.7	0.8350001	11.21298	0.0936284	0.00835	Y	YN	0	6	Yyn6	9.4	0.835	11.21298	0.0936284	0.00835
2 MVA 20/0.4 kV Yyn6 wnr 60 ASEA	Three Phase Transformer	2	60	20	0.4	9.4	16.7	0.8350001	11.21298	0.0936284	0.00835	Y	YN	0	6	Yyn6	9.4	0.835	11.21298	0.0936284	0.00835
2.5 MVA 20/0.4 kV Dyn0 wnr 60 ASEA	Three Phase Transformer	2.5	60	20	0.4	9.4	20	0.8	11.70737	0.09365895	0.008	D	YN	0	0	Dyn0	9.4	0.8	11.70737	0.09365895	0.008
2.5 MVA 20/0.4 kV Dyn1 60 ASEA	Three Phase Transformer	2.5	60	20	0.4	9.4	20	0.8	11.70737	0.09365895	0.008	D	YN	0	1	Dyn1	9.4	0.8	11.70737	0.09365895	0.008
2.5 MVA 20/0.4 kV Dyn1 wnr 60 ASEA	Three Phase Transformer	2.5	60	20	0.4	9.4	20	0.8	11.70737	0.09365895	0.008	D	YN	0	1	Dyn1	9.4	0.8	11.70737	0.09365895	0.008
2.5 MVA 20/0.4 kV Dyn11 60 ASEA	Three Phase Transformer	2.5	60	20	0.4	9.4	20	0.8	11.70737	0.09365895	0.008	D	YN	0	11	Dyn11	9.4	0.8	11.70737	0.09365895	0.008
2.5 MVA 20/0.4 kV Dyn11 wnr 60 ASEA	Three Phase Transformer	2.5	60	20	0.4	9.4	20	0.8	11.70737	0.09365895	0.008	D	YN	0	11	Dyn11	9.4	0.8	11.70737	0.09365895	0.008
2.5 MVA 20/0.4 kV Dyn5 60 ASEA	Three Phase Transformer	2.5	60	20	0.4	9.4	20	0.8	11.70737	0.09365895	0.008	D	YN	0	5	Dyn5	9.4	0.8	11.70737	0.09365895	0.008
2.5 MVA 20/0.4 kV Dyn7 60 ASEA	Three Phase Transformer	2.5	60	20	0.4	9.4	20	0.8	11.70737	0.09365895	0.008	D	YN	0	7	Dyn7	9.4	0.8	11.70737	0.09365895	0.008
2.5 MVA 20/0.4 kV Dyn7 wnr 60 ASEA	Three Phase Transformer	2.5	60	20	0.4	9.4	20	0.8	11.70737	0.09365895	0.008	D	YN	0	7	Dyn7	9.4	0.8	11.70737	0.09365895	0.008
2.5 MVA 20/0.4 kV Yyn0 60 ASEA	Three Phase Transformer	2.5	60	20	0.4	9.4	20	0.8	11.70737	0.09365895	0.008	Y	YN	0	0	Yyn0	9.4	0.8	11.70737	0.09365895	0.008
2.5 MVA 20/0.4 kV Yyn0 wnr 60 ASEA	Three Phase Transformer	2.5	60	20	0.4	9.4	20	0.8	11.70737	0.09365895	0.008	Y	YN	0	0	Yyn0	9.4	0.8	11.70737	0.09365895	0.008
2.5 MVA 20/0.4 kV Yyn6 60 ASEA	Three Phase Transformer	2.5	60	20	0.4	9.4	20	0.8	11.70737	0.09365895	0.008	Y	YN	0	6	Yyn6	9.4	0.8	11.70737	0.09365895	0.008
2.5 MVA 20/0.4 kV Yyn6 wnr 60 ASEA	Three Phase Transformer	2.5	60	20	0.4	9.4	20	0.8	11.70737	0.09365895	0.008	Y	YN	0	6	Yyn6	9.4	0.8	11.70737	0.09365895	0.008
10 MVA 69 +/- 2x2.5% /13.8 KV/FC	Three Phase Transformer	10	60	69	13.8	8	61.5	0.615	12.96964	0.07976326	0.00615	D	YN	0	1	Dyn1	8	0.615	12.96964	0.07976326	0.00615
10 MVA 69 +/- 2x2.5% /23.1 KV/FC	Three Phase Transformer	10	60	69	23.1	8	61.5	0.615	12.96964	0.07976326	0.00615	D	YN	0	1	Dyn1	8	0.615	12.96964	0.07976326	0.00615
10 MVA 69 +/- 8x1.25% /13.8 KV/FC	Three Phase Transformer	10	60	69	13.8	8	68	0.68	11.72213	0.07971048	0.0068	D	YN	0	1	Dyn1	8	0.68	11.72213	0.07971048	0.0068
10 MVA 69 +/- 8x1.25% /23.1 KV/FC	Three Phase Transformer	10	60	69	23.1	8	68	0.68	11.72213	0.07971048	0.0068	D	YN	0	1	Dyn1	8	0.68	11.72213	0.07971048	0.0068
15 MVA 69 +/- 2x2.5% /13.8 KV/FC	Three Phase Transformer	15	60	69	13.8	9	78	0.52	17.27878	0.08984965	0.0052	D	YN	0	1	Dyn1	9	0.52	17.27878	0.08984965	0.0052
15 MVA 69 +/- 2x2.5% /23.1 KV/FC	Three Phase Transformer	15	60	69	23.1	9	78	0.52	17.27878	0.08984965	0.0052	D	YN	0	1	Dyn1	9	0.52	17.27878	0.08984965	0.0052
15 MVA 69 +/- 8x1.25% /13.8 KV/FC	Three Phase Transformer	15	60	69	13.8	8	77.5	0.5166667	15.45155	0.07983299	0.00516667	D	YN	0	1	Dyn1	8	0.5166667	15.45154	0.07983299	0.00516667
15 MVA 69 +/- 8x1.25% /23.1 KV/FC	Three Phase Transformer	15	60	69	23.1	8	77.5	0.5166667	15.45155	0.07983299	0.00516667	D	YN	0	1	Dyn1	8	0.5166667	15.45154	0.07983299	0.00516667
20 MVA 69 +/- 2x2.5% /13.8 KV/FC	Three Phase Transformer	20	60	69	13.8	10	106	0.53	18.84141	0.09985945	0.0053	D	YN	0	1	Dyn1	10	0.53	18.84141	0.09985945	0.0053
20 MVA 69 +/- 2x2.5% /23.1 KV/FC	Three Phase Transformer	20	60	69	23.1	10	106	0.53	18.84141	0.09985945	0.0053	D	YN	0	1	Dyn1	10	0.53	18.84141	0.09985945	0.0053
20 MVA 69 +/- 8x1.25% /13.8 KV/FC	Three Phase Transformer	20	60	69	13.8	8	94	0.47	16.99188	0.07986182	0.0047	D	YN	0	1	Dyn1	8	0.47	16.99188	0.07986182	0.0047
20 MVA 69 +/- 8x1.25% /23.1 KV/FC	Three Phase Transformer	20	60	69	23.1	8	94	0.47	16.99188	0.07986182	0.0047	D	YN	0	1	Dyn1	8	0.47	16.99188	0.07986182	0.0047
25 MVA 69 +/- 2x2.5% /13.8 KV/FC	Three Phase Transformer	25	60	69	13.8	10	119	0.476	20.98459	0.09988665	0.00476	D	YN	0	1	Dyn1	10	0.476	20.98459	0.09988665	0.00476
25 MVA 69 +/- 2x2.5% /23.1 KV/FC	Three Phase Transformer	25	60	69	23.1	10	119	0.476	20.98459	0.09988665	0.00476	D	YN	0	1	Dyn1	10	0.476	20.98459	0.09988665	0.00476
25 MVA 69 +/- 8x1.25% /13.8 KV/FC	Three Phase Transformer	25	60	69	13.8	8	109	0.436	18.32135	0.0798811	0.00436	D	YN	0	1	Dyn1	8	0.436	18.32136	0.0798811	0.00436
25 MVA 69 +/- 8x1.25% /23.1 KV/FC	Three Phase Transformer	25	60	69	23.1	8	109	0.436	18.32135	0.0798811	0.00436	D	YN	0	1	Dyn1	8	0.436	18.32136	0.0798811	0.00436
30 MVA 69 +/- 2x2.5% /13.8 KV/FC	Three Phase Transformer	30	60	69	13.8	10	133	0.4433333	22.53421	0.09990168	0.00443333	D	YN	0	1	Dyn1	10	0.4433333	22.53422	0.09990168	0.00443333
30 MVA 69 +/- 2x2.5% /23.1 KV/FC	Three Phase Transformer	30	60	69	23.1	10	133	0.4433333	22.53421	0.09990168	0.00443333	D	YN	0	1	Dyn1	10	0.4433333	22.53422	0.09990168	0.00443333
30 MVA 69 +/- 8x1.25% /13.8 KV/FC	Three Phase Transformer	30	60	69	13.8	8	130	0.4333333	18.43444	0.07988255	0.00433333	D	YN	0	1	Dyn1	8	0.4333333	18.43444	0.07988255	0.00433333
30 MVA 69 +/- 8x1.25% /23.1 KV/FC	Three Phase Transformer	30	60	69	23.1	8	130	0.4333333	18.43444	0.07988255	0.00433333	D	YN	0	1	Dyn1	8	0.4333333	18.43444	0.07988255	0.00433333
5 MVA 69 +/- 2x2.5% /13.8 KV/FC	Three Phase Transformer	5	60	69	13.8	7	35	0.7	9.949874	0.06964912	0.007	D	YN	0	1	Dyn1	7	0.7	9.949875	0.06964912	0.007
5 MVA 69 +/- 2x2.5% /23.1 KV/FC	Three Phase Transformer	5	60	69	23.1	7	35	0.7	9.949874	0.06964912	0.007	D	YN	0	1	Dyn1	7	0.7	9.949875	0.06964912	0.007
5 MVA 69 +/- 8x1.25% /13.8 KV/FC	Three Phase Transformer	5	60	69	13.8	7	36	0.72	9.670657	0.06962873	0.0072	D	YN	0	1	Dyn1	7	0.72	9.670656	0.06962873	0.0072
5 MVA 69 +/- 8x1.25% /23.1 KV/FC	Three Phase Transformer	5	60	69	23.1	7	36	0.72	9.670657	0.06962873	0.0072	D	YN	0	1	Dyn1	7	0.72	9.670656	0.06962873	0.0072
7.5 MVA 69 +/- 2x2.5% /13.8 KV/FC	Three Phase Transformer	7.5	60	69	13.8	8	48.2	0.6426667	12.4079	0.07974144	0.00642667	D	YN	0	1	Dyn1	8	0.6426667	12.4079	0.07974144	0.00642667
7.5 MVA 69 +/- 2x2.5% /23.1 KV/FC	Three Phase Transformer	7.5	60	69	23.1	8	48.2	0.6426667	12.4079	0.07974144	0.00642667	D	YN	0	1	Dyn1	8	0.6426667	12.4079	0.07974144	0.00642667
7.5 MVA 69 +/- 8x1.25% /13.8 KV/FC	Three Phase Transformer	7.5	60	69	13.8	8	47	0.6266667	12.72673	0.07975417	0.00626667	D	YN	0	1	Dyn1	8	0.6266667	12.72673	0.07975417	0.00626667
7.5 MVA 69 +/- 8x1.25% /23.1 KV/FC	Three Phase Transformer	7.5	60	69	23.1	8	47	0.6266667	12.72673	0.07975417	0.00626667	D	YN	0	1	Dyn1	8	0.6266667	12.72673	0.07975417	0.00626667
10 MVA 138 +/- 2x2.5% /13.8 KV/FC	Three Phase Transformer	10	60	138	13.8	9	53.5	0.535	16.79268	0.08984084	0.00535	D	YN	0	1	Dyn1	9	0.535	16.79268	0.08984084	0.00535
10 MVA 138 +/- 2x2.5% /23.1 KV/FC	Three Phase Transformer	10	60	138	23.1	9	53.5	0.535	16.79268	0.08984084	0.00535	D	YN	0	1	Dyn1	9	0.535	16.79268	0.08984084	0.00535
10 MVA 138 +/- 8x1.25% /13.8 KV/FC	Three Phase Transformer	10	60	138	13.8	9	53.5	0.535	16.79268	0.08984084	0.00535	D	YN	0	1	Dyn1	9	0.535	16.79268	0.08984084	0.00535
10 MVA 138 +/- 8x1.25% /23.1 KV/FC	Three Phase Transformer	10	60	138	23.1	9	53.5	0.535	16.79268	0.08984084	0.00535	D	YN	0	1	Dyn1	9	0.535	16.79268	0.08984084	0.00535
15 MVA 138 +/- 2x2.5% /13.8 KV/FC	Three Phase Transformer	15	60	138	13.8	9	68	0.4533333	19.82774	0.08988576	0.00453333	D	YN	0	1	Dyn1	9	0.4533333	19.82774	0.08988576	0.00453333
15 MVA 138 +/- 2x2.5% /23.1 KV/FC	Three Phase Transformer	15	60	138	23.1	9	68	0.4533333	19.82774	0.08988576	0.00453333	D	YN	0	1	Dyn1	9	0.4533333	19.82774	0.08988576	0.00453333
15 MVA 138 +/- 8x1.25% /13.8 KV/FC	Three Phase Transformer	15	60	138	13.8	9	68	0.4533333	19.82774	0.08988576	0.00453333	D	YN	0	1	Dyn1	9	0.4533333	19.82774	0.08988576	0.00453333
15 MVA 138 +/- 8x1.25% /23.1 KV/FC	Three Phase Transformer	15	60	138	23.1	9	68	0.4533333	19.82774	0.08988576	0.00453333	D	YN	0	1	Dyn1	9	0.4533333	19.82774	0.08988576	0.00453333
20 MVA 138 +/- 2x2.5% /13.8 KV/FC	Three Phase Transformer	20	60	138	13.8	10	96	0.48	20.80932	0.09988473	0.0048	D	YN	0	1	Dyn1	10	0.48	20.80932	0.09988473	0.0048
20 MVA 138 +/- 2x2.5% /23.1 KV/FC	Three Phase Transformer	20	60	138	23.1	10	96	0.48	20.80932	0.09988473	0.0048	D	YN	0	1	Dyn1	10	0.48	20.80932	0.09988473	0.0048
20 MVA 138 +/- 8x1.25% /13.8 KV/FC	Three Phase Transformer	20	60	138	13.8	10	96	0.48	20.80932	0.09988473	0.0048	D	YN	0	1	Dyn1	10	0.48	20.80932	0.09988473	0.0048
20 MVA 138 +/- 8x1.25% /23.1 KV/FC	Three Phase Transformer	20	60	138	23.1	10	96	0.48	20.80932	0.09988473	0.0048	D	YN	0	1	Dyn1	10	0.48	20.80932	0.09988473	0.0048
25 MVA 138 +/- 2x2.5% /13.8 KV/FC	Three Phase Transformer	25	60	138	13.8	11	122	0.488	22.51879	0.1098917	0.00488	D	YN	0	1	Dyn1	11	0.488	22.51879	0.1098917	0.00488
25 MVA 138 +/- 2x2.5% /23.1 KV/FC	Three Phase Transformer	25	60	138	23.1	11	122	0.488	22.51879	0.1098917	0.00488	D	YN	0	1	Dyn1	11	0.488	22.51879	0.1098917	0.00488
25 MVA 138 +/- 8x1.25% /13.8 KV/FC	Three Phase Transformer	25	60	138	13.8	11	122	0.488	22.51879	0.1098917	0.00488	D	YN	0	1	Dyn1	11	0.488	22.51879	0.1098917	0.00488
25 MVA 138 +/- 8x1.25% /23.1 KV/FC	Three Phase Transformer	25	60	138	23.1	11	122	0.488	22.51879	0.1098917	0.00488	D	YN	0	1	Dyn1	11	0.488	22.51879	0.1098917	0.00488
30 MVA 138 +/- 2x2.5% /13.8 KV/FC	Three Phase Transformer	30	60	138	13.8	11	154	0.5133333	21.40523	0.1098802	0.00513333	D	YN	0	1	Dyn1	11	0.5133333	21.40523	0.1098802	0.00513333
30 MVA 138 +/- 2x2.5% /23.1 KV/FC	Three Phase Transformer	30	60	138	23.1	11	154	0.5133333	21.40523	0.1098802	0.00513333	D	YN	0	1	Dyn1	11	0.5133333	21.40523	0.1098802	0.00513333
30 MVA 138 +/- 8x1.25% /13.8 KV/FC	Three Phase Transformer	30	60	138	13.8	11	154	0.5133333	21.40523	0.1098802	0.00513333	D	YN	0	1	Dyn1	11	0.5133333	21.40523	0.1098802	0.00513333
30 MVA 138 +/- 8x1.25% /23.1 KV/FC	Three Phase Transformer	30	60	138	23.1	11	154	0.5133333	21.40523	0.1098802	0.00513333	D	YN	0	1	Dyn1	11	0.5133333	21.40523	0.1098802	0.00513333
5 MVA 138 +/- 2x2.5% /13.8 KV/FC	Three Phase Transformer	5	60	138	13.8	8	28	0.56	14.25067	0.07980376	0.0056	D	YN	0	1	Dyn1	8	0.56	14.25067	0.07980376	0.0056
5 MVA 138 +/- 2x2.5% /23.1 KV/FC	Three Phase Transformer	5	60	138	23.1	8	28	0.56	14.25067	0.07980376	0.0056	D	YN	0	1	Dyn1	8	0.56	14.25067	0.07980376	0.0056
5 MVA 138 +/- 8x1.25% /13.8 KV/FC	Three Phase Transformer	5	60	138	13.8	8	28	0.56	14.25067	0.07980376	0.0056	D	YN	0	1	Dyn1	8	0.56	14.25067	0.07980376	0.0056
5 MVA 138 +/- 8x1.25% /23.1 KV/FC	Three Phase Transformer	5	60	138	23.1	8	28	0.56	14.25067	0.07980376	0.0056	D	YN	0	1	Dyn1	8	0.56	14.25067	0.07980376	0.0056
7.5 MVA 138 +/- 2x2.5% /13.8 KV/FC	Three Phase Transformer	7.5	60	138	13.8	8	39	0.52	15.35208	0.07983082	0.0052	D	YN	0	1	Dyn1	8	0.52	15.35208	0.07983082	0.0052
7.5 MVA 138 +/- 2x2.5% /23.1 KV/FC	Three Phase Transformer	7.5	60	138	23.1	8	39	0.52	15.35208	0.07983082	0.0052	D	YN	0	1	Dyn1	8	0.52	15.35208	0.07983082	0.0052
7.5 MVA 138 +/- 8x1.25% /13.8 KV/FC	Three Phase Transformer	7.5	60	138	13.8	8	39	0.52	15.35208	0.07983082	0.0052	D	YN	0	1	Dyn1	8	0.52	15.35208	0.07983082	0.0052
7.5 MVA 138 +/- 8x1.25% /23.1 KV/FC	Three Phase Transformer	7.5	60	138	23.1	8	39	0.52	15.35208	0.07983082	0.0052	D	YN	0	1	Dyn1	8	0.52	15.35208	0.07983082	0.0052
210 MVA 132/15.75 kV	Three Phase Transformer	210	50	132	15.75	12.5	410	0.1952381	64.01658	0.1249847	0.00195238	YN	D	0	11	YNd11	10	0	9999999	0.1	0
25 MVA 20/10 kV	Three Phase Transformer	25	50	20	10	10.3	102.76	0.41104	25.03843	0.102918	0.0041104	YN	D	0	5	YNd5	9	0	9999999	0.09	0
255 MVA 380/19 kV	Three Phase Transformer	255	50	380	19	16	310	0.1215686	131.6091	0.1599954	0.00121569	YN	D	0	0	YNd0	13	0	9999999	0.13	0
47 MVA 33/11 kV	Three Phase Transformer	47	50	33	11	15	97	0.206383	72.67354	0.1499858	0.00206383	YN	YN	0	0	YNyn0	11	0	9999999	0.11	0
50 MVA 139/10.5 kV	Three Phase Transformer	50	50	139.3	10.5	10.08	188.098	0.376196	26.77587	0.1007298	0.00376196	YN	D	0	5	YNd5	9	0	9999999	0.09	0
55 MVA 139/10.5 kV	Three Phase Transformer	55	50	139.3	10.5	10.04	168.743	0.3068055	32.70904	0.1003531	0.00306805	YN	D	0	5	YNd5	9	0	9999999	0.09	0
90 MVA 132/33 kV	Three Phase Transformer	90	50	132	33	13.18	249.876	0.27764	47.46101	0.1317707	0.0027764	YN	D	0	1	YNd1	10	0	9999999	0.1	0

## Cables
Name	Rated voltage [kV]	Rated current [kA]	Nominal Frequency	Phases	Number of Neutrals	R' [Ohm/km AC,20°C]	X' [Ohm/km]	L' [Ohm/km]	R0'(AC) [Ohm/km]	X0' [Ohm/km]	L0' [mH/km]	Rn'(AC) [Ohm/km]	Xn' [Ohm/km]	Ln' [mH/km]	Rpn'(AC) [Ohm/km]	Xpn' [Ohm/km]	Lpn' [mH/km]
BD-FPE AL2-4x5 0.60 kV	0.6	1.8	50	3	0	0.00217	0.0014	0.004456	0.052	0.087	0.27693	0	0	0	0	0	0
BD-FPE AL2-4x6 0.60 kV	0.6	2.2	50	3	0	0.00194	0.00131	0.00417	0.243	0.149	0.474282	0	0	0	0	0	0
BD-FPE AL4-4x4 0.60 kV	0.6	2.6	50	3	0	0.0014	0.001	0.003183	0.173	0.123	0.391521	0	0	0	0	0	0
BD-FPE AL4-4x6 0.60 kV	0.6	3.6	50	3	0	0.00089	0.00071	0.00226	0.173	0.123	0.391521	0	0	0	0	0	0
BD-FPE CU2-4x4 0.60 kV	0.6	2	50	3	0	0.00168	0.00156	0.004966	0.084	0.132	0.420169	0	0	0	0	0	0
BD-FPE CU2-4x5 0.60 kV	0.6	2.3	50	3	0	0.00133	0.00137	0.004361	0.084	0.132	0.420169	0	0	0	0	0	0
BD-FPE CU2-4x6 0.60 kV	0.6	2.66	50	3	0	0.00122	0.00126	0.004011	0.091	0.093	0.296028	0	0	0	0	0	0
BD-FPE CU4-4x4 0.60 kV	0.6	3.56	50	3	0	0.00069	0.00101	0.003215	0.06	0.068	0.216451	0	0	0	0	0	0
BD-FPE CU4-4x5 0.60 kV	0.6	4.55	50	3	0	0.00079	0.00076	0.002419	0.06	0.06	0.190986	0	0	0	0	0	0
BD-IBER BB3000CU 1.00 kV	1	3	50	3	0	0.015	0.008	0.025465	0.094	0.17	0.541127	0	0	0	0	0	0
BD-IBER BV2500AL 1.00 kV	1	2.5	50	3	0	0.02	0.015	0.047746	0.125	0.319	1.015409	0	0	0	0	0	0
BD-KLOE-M LD1. 1.00 kV	1	1	50	3	0	0.047	0.034	0.108225	0.185	0.182	0.579324	0	0	0	0	0	0
BD-KLOE-M LD2. 1.00 kV	1	1.25	50	3	0	0.044	0.034	0.108225	0.183	0.18	0.572958	0	0	0	0	0	0
BD-KLOE-M LD2.CU 1.00 kV	1	1.55	50	3	0	0.029	0.045	0.143239	0.124	0.164	0.522028	0	0	0	0	0	0
BD-KLOE-M LD3. 1.00 kV	1	1.6	50	3	0	0.036	0.031	0.098676	0.137	0.138	0.439268	0	0	0	0	0	0
BD-KLOE-M LD3.CU 1.00 kV	1	2.05	50	3	0	0.024	0.037	0.117775	0.084	0.132	0.420169	0	0	0	0	0	0
BD-KLOE-M LD4. 1.00 kV	1	2.5	50	3	0	0.026	0.027	0.085944	0.147	0.094	0.299211	0	0	0	0	0	0
BD-KLOE-M LD4.CU 1.00 kV	1	2.7	50	3	0	0.017	0.028	0.089127	0.091	0.093	0.296028	0	0	0	0	0	0
BD-KLOE-M LD5. 1.00 kV	1	3.1	50	3	0	0.017	0.022	0.070028	0.11	0.077	0.245099	0	0	0	0	0	0
BD-KLOE-M LD5.CU 1.00 kV	1	3.5	50	3	0	0.01	0.014	0.044563	0.06	0.068	0.216451	0	0	0	0	0	0
BD-KLOE-M LDA1 1.00 kV	1	1.1	50	3	0	0.08	0.051	0.162338	0.078	0.087	0.27693	0	0	0	0	0	0
BD-KLOE-M LDA2 1.00 kV	1	1.25	50	3	0	0.048	0.046	0.146423	0.052	0.087	0.27693	0	0	0	0	0	0
BD-KLOE-M LDA3 1.00 kV	1	1.6	50	3	0	0.043	0.043	0.136873	0.052	0.087	0.27693	0	0	0	0	0	0
BD-KLOE-M LDA4 1.00 kV	1	2	50	3	0	0.039	0.028	0.089127	0.243	0.149	0.474282	0	0	0	0	0	0
BD-KLOE-M LDA5 1.00 kV	1	2.5	50	3	0	0.021	0.021	0.066845	0.173	0.123	0.391521	0	0	0	0	0	0
BD-KLOE-M LDA6 1.00 kV	1	3	50	3	0	0.021	0.023	0.073211	0.173	0.123	0.391521	0	0	0	0	0	0
BD-KLOE-M LDA7 1.00 kV	1	3.7	50	3	0	0.017	0.02	0.063662	0.121	0.098	0.311944	0	0	0	0	0	0
BD-KLOE-M LDC2 1.00 kV	1	2	50	3	0	0.03	0.044	0.140056	0.035	0.084	0.26738	0	0	0	0	0	0
BD-KLOE-M LDC3 1.00 kV	1	2.6	50	3	0	0.022	0.036	0.114592	0.028	0.071	0.226	0	0	0	0	0	0
BD-KLOE-M LDC6 1.00 kV	1	3.4	50	3	0	0.017	0.024	0.076394	0.104	0.113	0.35969	0	0	0	0	0	0
BD-KLOE-M LDC7 1.00 kV	1	4.4	50	3	0	0.013	0.017	0.054113	0.018	0.036	0.114592	0	0	0	0	0	0
BD-OTTERM U1250 0.66 kV	0.66	1.25	50	3	0	0.044	0.054	0.171887	0.052	0.087	0.27693	0	0	0	0	0	0
BD-OTTERM U1600 0.66 kV	0.66	1.6	50	3	0	0.031	0.042	0.13369	0.052	0.087	0.27693	0	0	0	0	0	0
BD-OTTERM U2000 0.66 kV	0.66	2	50	3	0	0.024	0.036	0.114592	0.243	0.149	0.474282	0	0	0	0	0	0
BD-OTTERM U2500 0.66 kV	0.66	2.5	50	3	0	0.02	0.033	0.105042	0.173	0.123	0.391521	0	0	0	0	0	0
BD-OTTERM U3500 0.66 kV	0.66	3.5	50	3	0	0.013	0.018	0.057296	0.035	0.084	0.26738	0	0	0	0	0	0
BD-TELEM KHF-14 0.75 kV	0.75	1	50	3	0	0.084	0.035	0.111408	0.06	0.06	0.190986	0	0	0	0	0	0
BD-TELEM KHF-16 0.75 kV	0.75	1.2	50	3	0	0.057	0.035	0.111408	0.158	0.157	0.499747	0	0	0	0	0	0
BD-TELEM KHF-18 0.75 kV	0.75	1.45	50	3	0	0.042	0.035	0.111408	0.122	0.157	0.499747	0	0	0	0	0	0
BD-TELEM KHF-26 0.75 kV	0.75	2.2	50	3	0	0.028	0.016	0.05093	0.078	0.059	0.187803	0	0	0	0	0	0
BD-TELEM KHF-28 0.75 kV	0.75	2.5	50	3	0	0.021	0.016	0.05093	0.06	0.059	0.187803	0	0	0	0	0	0
BD-TELEM KHF-36 0.75 kV	0.75	3	50	3	0	0.019	0.01	0.031831	0.052	0.033	0.105042	0	0	0	0	0	0
BD-TELEM KHF-38 0.75 kV	0.75	3.4	50	3	0	0.014	0.01	0.031831	0.04	0.033	0.105042	0	0	0	0	0	0
BD-TELEM KHF-46 0.75 kV	0.75	4	50	3	0	0.014	0.007	0.022282	0.039	0.024	0.076394	0	0	0	0	0	0
BD-TELEM KHF-48 0.75 kV	0.75	4.5	50	3	0	0.01	0.007	0.022282	0.03	0.024	0.076394	0	0	0	0	0	0
BD-TELEM KHF-56 0.75 kV	0.75	5	50	3	0	0.011	0.005	0.015915	0.03	0.019	0.060479	0	0	0	0	0	0
BD-TELEM KHF-58 0.75 kV	0.75	5.5	50	3	0	0.008	0.005	0.015915	0.023	0.019	0.060479	0	0	0	0	0	0
DROSS 1 6.00 kV	6	1	50	3	0	0.0276	0.2758	0.877899	0.001	0	0	0	0	0	0	0	0
EIAJB 3x120 15.00 kV	15	0.283	50	3	0	0.153	0.11	0.350141	1	1	3.183099	0	0	0	0	0	0
EIAJB 3x150 15.00 kV	15	0.316	50	3	0	0.124	0.106	0.337408	1	1	3.183099	0	0	0	0	0	0
EIAJB 3x185 15.00 kV	15	0.358	50	3	0	0.0991	0.103	0.327859	1	1	3.183099	0	0	0	0	0	0
EIAJB 3x240 15.00 kV	15	0.416	50	3	0	0.0754	0.101	0.321493	1	1	3.183099	0	0	0	0	0	0
EIAJB 3x25 15.00 kV	15	0.12	50	3	0	0.727	0.143	0.455183	1	1	3.183099	0	0	0	0	0	0
EIAJB 3x35 15.00 kV	15	0.144	50	3	0	0.524	0.136	0.432901	1	1	3.183099	0	0	0	0	0	0
EIAJB 3x50 15.00 kV	15	0.171	50	3	0	0.367	0.129	0.41062	1	1	3.183099	0	0	0	0	0	0
EIAJB 3x70 15.00 kV	15	0.209	50	3	0	0.268	0.123	0.391521	1	1	3.183099	0	0	0	0	0	0
EIAJB 3x95 15.00 kV	15	0.249	50	3	0	0.193	0.113	0.35969	1	1	3.183099	0	0	0	0	0	0
KUP 1 6.00 kV	6	1.2	50	3	0	0.001	0.001	0.003183	0.001	0.001	0.003183	0	0	0	0	0	0
KUP 1 25.00 kV	25	1.2	50	3	0	0.001	0.001	0.003183	0.001	0.001	0.003183	0	0	0	0	0	0
N2XS2Y 1x120 20.00 kV	20	0.368	50	3	0	0.153	0.125	0.397887	1.003	0.546	1.737972	0	0	0	0	0	0
N2XS2Y 1x150 20.00 kV	20	0.41	50	3	0	0.124	0.121	0.385155	0.765	0.297	0.94538	0	0	0	0	0	0
N2XS2Y 1x185 20.00 kV	20	0.462	50	3	0	0.0991	0.117	0.372423	0.739	0.294	0.935831	0	0	0	0	0	0
N2XS2Y 1x240 20.00 kV	20	0.534	50	3	0	0.0754	0.112	0.356507	0.715	0.291	0.926282	0	0	0	0	0	0
N2XS2Y 1x25 20.00 kV	20	0.159	50	3	0	0.727	0.16	0.509296	1.588	0.572	1.820733	0	0	0	0	0	0
N2XS2Y 1x35 20.00 kV	20	0.189	50	3	0	0.524	0.152	0.483831	1.383	0.566	1.801634	0	0	0	0	0	0
N2XS2Y 1x50 20.00 kV	20	0.223	50	3	0	0.387	0.145	0.461549	1.244	0.56	1.782535	0	0	0	0	0	0
N2XS2Y 1x70 20.00 kV	20	0.272	50	3	0	0.268	0.137	0.436085	1.122	0.554	1.763437	0	0	0	0	0	0
N2XS2Y 1x95 20.00 kV	20	0.324	50	3	0	0.193	0.13	0.413803	1.045	0.549	1.747521	0	0	0	0	0	0
N2XSY 1X500 10kV DE	10	0.739	50	3	0	0.046	0.096	0.3055775	1	1	3.183099	0	0	0	0	0	0
N2XSY 1x120 10.00 kV	10	0.364	50	3	0	0.154	0.117	0.372423	1.009	0.533	1.696592	0	0	0	0	0	0
N2XSY 1x120 20.00 kV	20	0.368	50	3	0	0.154	0.125	0.397887	1.003	0.546	1.737972	0	0	0	0	0	0
N2XSY 1x150 10.00 kV	10	0.405	50	3	0	0.127	0.113	0.35969	0.767	0.285	0.907183	0	0	0	0	0	0
N2XSY 1x150 20.00 kV	20	0.41	50	3	0	0.127	0.121	0.385155	0.765	0.297	0.94538	0	0	0	0	0	0
N2XSY 1x185 10.00 kV	10	0.457	50	3	0	0.103	0.11	0.350141	0.742	0.283	0.900817	0	0	0	0	0	0
N2XSY 1x185 20.00 kV	20	0.463	50	3	0	0.102	0.117	0.372423	0.739	0.294	0.935831	0	0	0	0	0	0
N2XSY 1x240 10.00 kV	10	0.528	50	3	0	0.08	0.105	0.334225	0.717	0.281	0.894451	0	0	0	0	0	0
N2XSY 1x240 20.00 kV	20	0.534	50	3	0	0.08	0.112	0.356507	0.715	0.291	0.926282	0	0	0	0	0	0
N2XSY 1x25 10.00 kV	10	0.157	50	3	0	0.711	0.149	0.474282	1.595	0.555	1.76662	0	0	0	0	0	0
N2XSY 1x25 20.00 kV	20	0.159	50	3	0	0.711	0.16	0.509296	1.588	0.572	1.820733	0	0	0	0	0	0
N2XSY 1x300 10.00 kV	10	0.593	50	3	0	0.065	0.102	0.324676	0.7	0.279	0.888085	0	0	0	0	0	0
N2XSY 1x300 20.00 kV	20	0.601	50	3	0	0.065	0.109	0.346958	0.698	0.289	0.919916	0	0	0	0	0	0
N2XSY 1x35 10.00 kV	10	0.187	50	3	0	0.518	0.142	0.452	1.39	0.549	1.747521	0	0	0	0	0	0
N2XSY 1x35 20.00 kV	20	0.189	50	3	0	0.518	0.152	0.483831	1.383	0.566	1.801634	0	0	0	0	0	0
N2XSY 1x400 10.00 kV	10	0.665	50	3	0	0.055	0.098	0.311944	0.536	0.525	1.671127	0	0	0	0	0	0
N2XSY 1x400 20.00 kV	20	0.674	50	3	0	0.054	0.105	0.334225	0.535	0.179	0.569775	0	0	0	0	0	0
N2XSY 1x50 10.00 kV	10	0.22	50	3	0	0.383	0.135	0.429718	1.251	0.544	1.731606	0	0	0	0	0	0
N2XSY 1x50 20.00 kV	20	0.223	50	3	0	0.382	0.145	0.461549	1.244	0.56	1.782535	0	0	0	0	0	0
N2XSY 1x500 20.00 kV	20	0.75	50	3	0	0.045	0.102	0.324676	0.524	0.177	0.563408	0	0	0	0	0	0
N2XSY 1x70 10.00 kV	10	0.269	50	3	0	0.266	0.127	0.404254	1.129	0.539	1.71569	0	0	0	0	0	0
N2XSY 1x70 20.00 kV	20	0.273	50	3	0	0.265	0.137	0.436085	1.122	0.554	1.763437	0	0	0	0	0	0
N2XSY 1x95 10.00 kV	10	0.321	50	3	0	0.193	0.122	0.388338	1.051	0.536	1.706141	0	0	0	0	0	0
N2XSY 1x95 20.00 kV	20	0.325	50	3	0	0.192	0.13	0.413803	1.045	0.549	1.747521	0	0	0	0	0	0
N2XSY 3x120 10.00 kV	10	0.349	50	3	0	0.155	0.092	0.292845	1	1	3.183099	0	0	0	0	0	0
N2XSY 3x150 10.00 kV	10	0.392	50	3	0	0.126	0.09	0.286479	1	1	3.183099	0	0	0	0	0	0
N2XSY 3x185 10.00 kV	10	0.443	50	3	0	0.102	0.087	0.27693	1	1	3.183099	0	0	0	0	0	0
N2XSY 3x240 10.00 kV	10	0.513	50	3	0	0.078	0.084	0.26738	1	1	3.183099	0	0	0	0	0	0
N2XSY 3x300 10.00 kV	10	0.579	50	3	0	0.063	0.082	0.261014	1	1	3.183099	0	0	0	0	0	0
N2XSY 3x35 10.00 kV	10	0.178	50	3	0	0.525	0.111	0.353324	1	1	3.183099	0	0	0	0	0	0
N2XSY 3x50 10.00 kV	10	0.21	50	3	0	0.387	0.106	0.337408	1	1	3.183099	0	0	0	0	0	0
N2XSY 3x70 10.00 kV	10	0.256	50	3	0	0.269	0.1	0.31831	1	1	3.183099	0	0	0	0	0	0
N2XSY 3x95 10.00 kV	10	0.307	50	3	0	0.194	0.095	0.302394	1	1	3.183099	0	0	0	0	0	0
N2YSY 1x120 20.00 kV	20	0.343	50	3	0	0.153	0.125	0.397887	1	1	3.183099	0	0	0	0	0	0
N2YSY 1x150 20.00 kV	20	0.381	50	3	0	0.127	0.121	0.385155	1	1	3.183099	0	0	0	0	0	0
N2YSY 1x185 20.00 kV	20	0.43	50	3	0	0.103	0.117	0.372423	1	1	3.183099	0	0	0	0	0	0
N2YSY 1x240 20.00 kV	20	0.496	50	3	0	0.079	0.112	0.356507	1	1	3.183099	0	0	0	0	0	0
N2YSY 1x25 20.00 kV	20	0.148	50	3	0	0.711	0.16	0.509296	1	1	3.183099	0	0	0	0	0	0
N2YSY 1x300 20.00 kV	20	0.556	50	3	0	0.065	0.109	0.346958	1	1	3.183099	0	0	0	0	0	0
N2YSY 1x35 20.00 kV	20	0.176	50	3	0	0.517	0.152	0.483831	1	1	3.183099	0	0	0	0	0	0
N2YSY 1x400 20.00 kV	20	0.623	50	3	0	0.055	0.105	0.334225	1	1	3.183099	0	0	0	0	0	0
N2YSY 1x50 20.00 kV	20	0.208	50	3	0	0.382	0.145	0.461549	1	1	3.183099	0	0	0	0	0	0
N2YSY 1x500 20.00 kV	20	0.692	50	3	0	0.046	0.102	0.324676	1	1	3.183099	0	0	0	0	0	0
N2YSY 1x70 20.00 kV	20	0.254	50	3	0	0.265	0.137	0.436085	1	1	3.183099	0	0	0	0	0	0
N2YSY 1x95 20.00 kV	20	0.302	50	3	0	0.193	0.13	0.413803	1	1	3.183099	0	0	0	0	0	0
NA2XSY 1x120 10.00 kV	10	0.283	50	3	0	0.251	0.117	0.372423	1.069	0.548	1.744338	0	0	0	0	0	0
NA2XSY 1x120 20.00 kV	20	0.287	50	3	0	0.251	0.125	0.397887	1.065	0.56	1.782535	0	0	0	0	0	0
NA2XSY 1x150 10.00 kV	10	0.316	50	3	0	0.207	0.113	0.35969	0.833	0.293	0.932648	0	0	0	0	0	0
NA2XSY 1x150 20.00 kV	20	0.32	50	3	0	0.207	0.121	0.385155	0.832	0.309	0.983577	0	0	0	0	0	0
NA2XSY 1x185 10.00 kV	10	0.358	50	3	0	0.166	0.11	0.350141	0.791	0.296	0.942197	0	0	0	0	0	0
NA2XSY 1x185 20.00 kV	20	0.362	50	3	0	0.166	0.117	0.372423	0.789	0.306	0.974028	0	0	0	0	0	0
NA2XSY 1x240 10.00 kV	10	0.416	50	3	0	0.128	0.105	0.334225	0.751	0.293	0.932648	0	0	0	0	0	0
NA2XSY 1x240 20.00 kV	20	0.421	50	3	0	0.127	0.112	0.356507	0.749	0.303	0.964479	0	0	0	0	0	0
NA2XSY 1x300 10.00 kV	10	0.469	50	3	0	0.104	0.102	0.324676	0.725	0.291	0.926282	0	0	0	0	0	0
NA2XSY 1x300 20.00 kV	20	0.474	50	3	0	0.102	0.109	0.346958	0.724	0.301	0.958113	0	0	0	0	0	0
NA2XSY 1x35 10.00 kV	10	0.144	50	3	0	0.859	0.142	0.452	1.691	0.566	1.801634	0	0	0	0	0	0
NA2XSY 1x35 20.00 kV	20	0.146	50	3	0	0.859	0.152	0.483831	1.686	0.581	1.84938	0	0	0	0	0	0
NA2XSY 1x400 10.00 kV	10	0.532	50	3	0	0.083	0.098	0.311944	0.56	0.179	0.569775	0	0	0	0	0	0
NA2XSY 1x400 20.00 kV	20	0.538	50	3	0	0.083	0.105	0.334225	0.56	0.186	0.592056	0	0	0	0	0	0
NA2XSY 1x50 10.00 kV	10	0.171	50	3	0	0.632	0.135	0.429718	1.462	0.561	1.785718	0	0	0	0	0	0
NA2XSY 1x50 20.00 kV	20	0.173	50	3	0	0.631	0.145	0.461549	1.458	0.575	1.830282	0	0	0	0	0	0
NA2XSY 1x500 10.00 kV	10	0.599	50	3	0	0.068	0.096	0.305577	0.543	0.177	0.563408	0	0	0	0	0	0
NA2XSY 1x500 20.00 kV	20	0.606	50	3	0	0.068	0.102	0.324676	0.542	0.184	0.58569	0	0	0	0	0	0
NA2XSY 1x70 10.00 kV	10	0.209	50	3	0	0.438	0.127	0.404254	1.262	0.555	1.76662	0	0	0	0	0	0
NA2XSY 1x70 20.00 kV	20	0.211	50	3	0	0.438	0.137	0.436085	1.258	0.568	1.808	0	0	0	0	0	0
NA2XSY 1x95 10.00 kV	10	0.249	50	3	0	0.317	0.122	0.388338	1.138	0.551	1.753887	0	0	0	0	0	0
NA2XSY 1x95 20.00 kV	20	0.252	50	3	0	0.316	0.13	0.413803	1.134	0.563	1.792085	0	0	0	0	0	0
NA2XSY 3x120 10.00 kV	10	0.271	50	3	0	0.255	0.092	0.292845	1	1	3.183099	0	0	0	0	0	0
NA2XSY 3x150 10.00 kV	10	0.304	50	3	0	0.208	0.09	0.286479	1	1	3.183099	0	0	0	0	0	0
NA2XSY 3x185 10.00 kV	10	0.345	50	3	0	0.166	0.087	0.27693	1	1	3.183099	0	0	0	0	0	0
NA2XSY 3x240 10.00 kV	10	0.401	50	3	0	0.127	0.084	0.26738	1	1	3.183099	0	0	0	0	0	0
NA2XSY 3x300 10.00 kV	10	0.453	50	3	0	0.103	0.082	0.261014	1	1	3.183099	0	0	0	0	0	0
NA2XSY 3x50 10.00 kV	10	0.162	50	3	0	0.642	0.106	0.337408	1	1	3.183099	0	0	0	0	0	0
NA2XSY 3x70 10.00 kV	10	0.199	50	3	0	0.444	0.1	0.31831	1	1	3.183099	0	0	0	0	0	0
NA2XSY 3x95 10.00 kV	10	0.238	50	3	0	0.321	0.095	0.302394	1	1	3.183099	0	0	0	0	0	0
NA2YSY 1x120 20.00 kV	20	0.267	50	3	0	0.251	0.125	0.397887	1	1	3.183099	0	0	0	0	0	0
NA2YSY 1x150 20.00 kV	20	0.298	50	3	0	0.207	0.121	0.385155	1	1	3.183099	0	0	0	0	0	0
NA2YSY 1x185 20.00 kV	20	0.337	50	3	0	0.166	0.117	0.372423	1	1	3.183099	0	0	0	0	0	0
NA2YSY 1x240 20.00 kV	20	0.391	50	3	0	0.127	0.112	0.356507	1	1	3.183099	0	0	0	0	0	0
NA2YSY 1x300 20.00 kV	20	0.44	50	3	0	0.104	0.109	0.346958	1	1	3.183099	0	0	0	0	0	0
NA2YSY 1x35 20.00 kV	20	0.136	50	3	0	0.869	0.152	0.483831	1	1	3.183099	0	0	0	0	0	0
NA2YSY 1x400 20.00 kV	20	0.499	50	3	0	0.083	0.105	0.334225	1	1	3.183099	0	0	0	0	0	0
NA2YSY 1x50 20.00 kV	20	0.161	50	3	0	0.631	0.145	0.461549	1	1	3.183099	0	0	0	0	0	0
NA2YSY 1x500 20.00 kV	20	0.562	50	3	0	0.068	0.102	0.324676	1	1	3.183099	0	0	0	0	0	0
NA2YSY 1x70 20.00 kV	20	0.197	50	3	0	0.438	0.137	0.436085	1	1	3.183099	0	0	0	0	0	0
NA2YSY 1x95 20.00 kV	20	0.235	50	3	0	0.316	0.13	0.413803	1	1	3.183099	0	0	0	0	0	0
NAEKEBA 3x120 20.00 kV	20	0.237	50	3	0	0.256	0.126	0.40107	1.5	0.25	0.795775	0	0	0	0	0	0
NAEKEBA 3x150 20.00 kV	20	0.267	50	3	0	0.21	0.122	0.388338	1.4	0.22	0.700282	0	0	0	0	0	0
NAEKEBA 3x185 20.00 kV	20	0.304	50	3	0	0.168	0.118	0.375606	1.3	0.21	0.668451	0	0	0	0	0	0
NAEKEBA 3x240 20.00 kV	20	0.355	50	3	0	0.13	0.114	0.362873	1.21	0.2	0.63662	0	0	0	0	0	0
NAEKEBA 3x300 20.00 kV	20	0.403	50	3	0	0.106	0.111	0.353324	1	1	3.183099	0	0	0	0	0	0
NAEKEBA 3x50 20.00 kV	20	0.14	50	3	0	0.644	0.146	0.464732	2.15	0.4	1.27324	0	0	0	0	0	0
NAEKEBA 3x70 20.00 kV	20	0.173	50	3	0	0.446	0.137	0.436085	1.95	0.35	1.114085	0	0	0	0	0	0
NAEKEBA 3x95 20.00 kV	20	0.208	50	3	0	0.323	0.131	0.416986	1.73	0.3	0.95493	0	0	0	0	0	0
NAKBA 3x120 10.00 kV	10	0.229	50	3	0	0.256	0.097	0.308761	2.4	1	3.183099	0	0	0	0	0	0
NAKBA 3x120/70 1.00 kV	1	0.249	50	3	0	0.255	0.083	0.264197	1.584	0.35	1.114085	0	0	0	0	0	0
NAKBA 3x150 10.00 kV	10	0.259	50	3	0	0.21	0.094	0.299211	2.1	1	3.183099	0	0	0	0	0	0
NAKBA 3x150/70 1.00 kV	1	0.281	50	3	0	0.208	0.084	0.26738	1.531	0.377	1.200028	0	0	0	0	0	0
NAKBA 3x185 10.00 kV	10	0.295	50	3	0	0.168	0.092	0.292845	1.8	1	3.183099	0	0	0	0	0	0
NAKBA 3x185/95 1.00 kV	1	0.32	50	3	0	0.167	0.083	0.264197	1.124	0.361	1.149099	0	0	0	0	0	0
NAKBA 3x240 10.00 kV	10	0.343	50	3	0	0.13	0.089	0.283296	1.48	1	3.183099	0	0	0	0	0	0
NAKBA 3x240/120 1.00 kV	1	0.372	50	3	0	0.131	0.082	0.261014	0.899	0.361	1.149099	0	0	0	0	0	0
NAKBA 3x25/16 1.00 kV	1	0.103	50	3	0	1.201	0.092	0.292845	6.87	0.408	1.298704	0	0	0	0	0	0
NAKBA 3x300 10.00 kV	10	0.389	50	3	0	0.106	0.087	0.27693	1	1	3.183099	0	0	0	0	0	0
NAKBA 3x300/150 1.00 kV	1	0.42	50	3	0	0.107	0.082	0.261014	0.737	0.354	1.126817	0	0	0	0	0	0
NAKBA 3x35/16 1.00 kV	1	0.124	50	3	0	0.876	0.09	0.286479	6.535	0.422	1.343268	0	0	0	0	0	0
NAKBA 3x50 10.00 kV	10	0.132	50	3	0	0.643	0.109	0.346958	3.4	1	3.183099	0	0	0	0	0	0
NAKBA 3x50/25 1.00 kV	1	0.148	50	3	0	0.642	0.087	0.27693	4.237	0.397	1.26369	0	0	0	0	0	0
NAKBA 3x70 10.00 kV	10	0.165	50	3	0	0.446	0.104	0.331042	3.1	1	3.183099	0	0	0	0	0	0
NAKBA 3x70/35 1.00 kV	1	0.182	50	3	0	0.444	0.085	0.270563	3.072	0.383	1.219127	0	0	0	0	0	0
NAKBA 3x95 10.00 kV	10	0.2	50	3	0	0.323	0.1	0.31831	2.8	1	3.183099	0	0	0	0	0	0
NAKBA 3x95/50 1.00 kV	1	0.218	50	3	0	0.321	0.084	0.26738	2.237	0.367	1.168197	0	0	0	0	0	0
NAKBA 4x120 1.00 kV	1	0.249	50	3	0	0.255	0.085	0.270563	1.02	0.299	0.951747	0	0	0	0	0	0
NAKBA 4x150 1.00 kV	1	0.281	50	3	0	0.208	0.086	0.273747	0.832	0.305	0.970845	0	0	0	0	0	0
NAKBA 4x16 1.00 kV	1	0.079	50	3	0	1.891	0.099	0.315127	7.564	0.401	1.276423	0	0	0	0	0	0
NAKBA 4x185 1.00 kV	1	0.32	50	3	0	0.167	0.085	0.270563	0.668	0.298	0.948563	0	0	0	0	0	0
NAKBA 4x240 1.00 kV	1	0.372	50	3	0	0.131	0.084	0.26738	0.524	0.295	0.939014	0	0	0	0	0	0
NAKBA 4x25 1.00 kV	1	0.103	50	3	0	1.201	0.094	0.299211	4.804	0.366	1.165014	0	0	0	0	0	0
NAKBA 4x300 1.00 kV	1	0.42	50	3	0	0.107	0.084	0.26738	0.428	0.289	0.919916	0	0	0	0	0	0
NAKBA 4x35 1.00 kV	1	0.124	50	3	0	0.876	0.092	0.292845	3.504	0.348	1.107718	0	0	0	0	0	0
NAKBA 4x50 1.00 kV	1	0.148	50	3	0	0.642	0.09	0.286479	2.568	0.332	1.056789	0	0	0	0	0	0
NAKBA 4x70 1.00 kV	1	0.182	50	3	0	0.444	0.087	0.27693	1.776	0.318	1.012225	0	0	0	0	0	0
NAKBA 4x95 1.00 kV	1	0.218	50	3	0	0.321	0.086	0.273747	1.284	0.307	0.977211	0	0	0	0	0	0
NAYCWY 4x120/70 1.00 kV	1	0.242	50	3	0	0.255	0.08	0.254648	1.02	0.292	0.929465	0	0	0	0	0	0
NAYCWY 4x150/70 1.00 kV	1	0.27	50	3	0	0.208	0.08	0.254648	0.832	0.292	0.929465	0	0	0	0	0	0
NAYCWY 4x185/95 1.00 kV	1	0.308	50	3	0	0.167	0.08	0.254648	0.668	0.292	0.929465	0	0	0	0	0	0
NAYCWY 4x35/16 1.00 kV	1	0.118	50	3	0	0.876	0.083	0.264197	3.504	0.343	1.091803	0	0	0	0	0	0
NAYCWY 4x50/25 1.00 kV	1	0.142	50	3	0	0.642	0.083	0.264197	2.568	0.312	0.993127	0	0	0	0	0	0
NAYCWY 4x70/35 1.00 kV	1	0.176	50	3	0	0.444	0.082	0.261014	1.776	0.3	0.95493	0	0	0	0	0	0
NAYCWY 4x95/50 1.00 kV	1	0.211	50	3	0	0.321	0.082	0.261014	1.284	0.299	0.951747	0	0	0	0	0	0
NAYFGBY 3x120 6.00 kV	6	0.243	50	3	0	0.255	0.096	0.305577	1	1	3.183099	0	0	0	0	0	0
NAYFGBY 3x150 6.00 kV	6	0.274	50	3	0	0.208	0.093	0.296028	1	1	3.183099	0	0	0	0	0	0
NAYFGBY 3x185 6.00 kV	6	0.31	50	3	0	0.167	0.091	0.289662	1	1	3.183099	0	0	0	0	0	0
NAYFGBY 3x240 6.00 kV	6	0.361	50	3	0	0.129	0.088	0.280113	1	1	3.183099	0	0	0	0	0	0
NAYFGBY 3x300 6.00 kV	6	0.408	50	3	0	0.105	0.086	0.273747	1	1	3.183099	0	0	0	0	0	0
NAYFGBY 3x50 6.00 kV	6	0.145	50	3	0	0.643	0.109	0.346958	1	1	3.183099	0	0	0	0	0	0
NAYFGBY 3x70 6.00 kV	6	0.178	50	3	0	0.445	0.103	0.327859	1	1	3.183099	0	0	0	0	0	0
NAYFGBY 3x95 6.00 kV	6	0.214	50	3	0	0.322	0.099	0.315127	1	1	3.183099	0	0	0	0	0	0
NAYSEY 3x300 10.00 kV	10	0.401	50	3	0	0.1	0.087	0.27693	1	1	3.183099	0	0	0	0	0	0
NAYY 4x120 1.00 kV	1	0.242	50	3	0	0.255	0.08	0.254648	1.02	0.292	0.929465	0	0	0	0	0	0
NAYY 4x150 1.00 kV	1	0.27	50	3	0	0.208	0.08	0.254648	0.832	0.292	0.929465	0	0	0	0	0	0
NAYY 4x185 1.00 kV	1	0.308	50	3	0	0.167	0.08	0.254648	0.668	0.292	0.929465	0	0	0	0	0	0
NAYY 4x35 1.00 kV	1	0.118	50	3	0	0.876	0.083	0.264197	3.504	0.343	1.091803	0	0	0	0	0	0
NAYY 4x50 1.00 kV	1	0.142	50	3	0	0.642	0.083	0.264197	2.568	0.312	0.993127	0	0	0	0	0	0
NAYY 4x70 1.00 kV	1	0.176	50	3	0	0.444	0.082	0.261014	1.776	0.3	0.95493	0	0	0	0	0	0
NAYY 4x95 1.00 kV	1	0.211	50	3	0	0.321	0.082	0.261014	1.284	0.299	0.951747	0	0	0	0	0	0
NEKEBA 3x120 20.00 kV	20	0.304	50	3	0	0.157	0.126	0.40107	1.4	0.25	0.795775	0	0	0	0	0	0
NEKEBA 3x150 20.00 kV	20	0.343	50	3	0	0.128	0.122	0.388338	1.3	0.22	0.700282	0	0	0	0	0	0
NEKEBA 3x185 20.00 kV	20	0.388	50	3	0	0.103	0.118	0.375606	1.2	0.21	0.668451	0	0	0	0	0	0
NEKEBA 3x240 20.00 kV	20	0.453	50	3	0	0.081	0.114	0.362873	1.15	0.2	0.63662	0	0	0	0	0	0
NEKEBA 3x25 20.00 kV	20	0.126	50	3	0	0.724	0.161	0.512479	1	1	3.183099	0	0	0	0	0	0
NEKEBA 3x300 20.00 kV	20	0.511	50	3	0	0.066	0.111	0.353324	1	1	3.183099	0	0	0	0	0	0
NEKEBA 3x35 20.00 kV	20	0.151	50	3	0	0.526	0.153	0.487014	1	1	3.183099	0	0	0	0	0	0
NEKEBA 3x50 20.00 kV	20	0.18	50	3	0	0.39	0.146	0.464732	2	0.4	1.27324	0	0	0	0	0	0
NEKEBA 3x70 20.00 kV	20	0.222	50	3	0	0.271	0.137	0.436085	1.8	0.35	1.114085	0	0	0	0	0	0
NEKEBA 3x95 20.00 kV	20	0.268	50	3	0	0.197	0.131	0.416986	1.6	0.3	0.95493	0	0	0	0	0	0
NKBA 3X 16 10kV E	10	0.09	50	3	0	1.12	0.132	0.4201691	1	1	3.183099	0	0	0	0	0	0
NKBA 3X 25 10kV E	10	0.117	50	3	0	0.714	0.122	0.3883381	1	1	3.183099	0	0	0	0	0	0
NKBA 3X 25/ 16 1kV-TN	1	0.133	50	3	0	0.724	0.092	0.2928451	4.148	0.408	1.298704	0	0	0	0	0	0
NKBA 3X 25/ 16 1kV-TT	1	0.133	50	3	0	0.724	0.092	0.2928451	1.672	1.523	4.847859	0	0	0	0	0	0
NKBA 3x120 10.00 kV	10	0.293	50	3	0	0.157	0.097	0.308761	2.3	1	3.183099	0	0	0	0	0	0
NKBA 3x120/70 1.00 kV	1	0.32	50	3	0	0.157	0.083	0.264197	0.97	0.35	1.114085	0	0	0	0	0	0
NKBA 3x150 10.00 kV	10	0.332	50	3	0	0.128	0.094	0.299211	2	1	3.183099	0	0	0	0	0	0
NKBA 3x150/70 1.00 kV	1	0.361	50	3	0	0.127	0.084	0.26738	0.927	0.377	1.200028	0	0	0	0	0	0
NKBA 3x185 10.00 kV	10	0.377	50	3	0	0.103	0.092	0.292845	1.7	1	3.183099	0	0	0	0	0	0
NKBA 3x185/95 1.00 kV	1	0.41	50	3	0	0.103	0.083	0.264197	0.68	0.361	1.149099	0	0	0	0	0	0
NKBA 3x240 10.00 kV	10	0.437	50	3	0	0.081	0.089	0.283296	1.4	1	3.183099	0	0	0	0	0	0
NKBA 3x240/120 1.00 kV	1	0.474	50	3	0	0.08	0.082	0.261014	0.539	0.361	1.149099	0	0	0	0	0	0
NKBA 3x300 10.00 kV	10	0.493	50	3	0	0.067	0.087	0.27693	1	1	3.183099	0	0	0	0	0	0
NKBA 3x300/150 1.00 kV	1	0.533	50	3	0	0.066	0.082	0.261014	0.442	0.354	1.126817	0	0	0	0	0	0
NKBA 3x35 10.00 kV	10	0.143	50	3	0	0.526	0.115	0.366056	1	1	3.183099	0	0	0	0	0	0
NKBA 3x35/16 1.00 kV	1	0.161	50	3	0	0.526	0.09	0.286479	3.95	0.422	1.343268	0	0	0	0	0	0
NKBA 3x50 10.00 kV	10	0.171	50	3	0	0.39	0.109	0.346958	3.2	1	3.183099	0	0	0	0	0	0
NKBA 3x50/25 1.00 kV	1	0.191	50	3	0	0.389	0.087	0.27693	2.56	0.397	1.26369	0	0	0	0	0	0
NKBA 3x70 10.00 kV	10	0.212	50	3	0	0.271	0.104	0.331042	2.9	1	3.183099	0	0	0	0	0	0
NKBA 3x70/35 1.00 kV	1	0.235	50	3	0	0.271	0.085	0.270563	1.848	0.383	1.219127	0	0	0	0	0	0
NKBA 3x95 10.00 kV	10	0.257	50	3	0	0.196	0.1	0.31831	2.6	1	3.183099	0	0	0	0	0	0
NKBA 3x95/50 1.00 kV	1	0.281	50	3	0	0.197	0.084	0.26738	1.369	0.367	1.168197	0	0	0	0	0	0
NKBA 4x120 1.00 kV	1	0.32	50	3	0	0.157	0.085	0.270563	0.628	0.299	0.951747	0	0	0	0	0	0
NKBA 4x150 1.00 kV	1	0.361	50	3	0	0.125	0.086	0.273747	0.5	0.305	0.970845	0	0	0	0	0	0
NKBA 4x16 1.00 kV	1	0.105	50	3	0	1.141	0.099	0.315127	4.564	0.401	1.276423	0	0	0	0	0	0
NKBA 4x185 1.00 kV	1	0.41	50	3	0	0.101	0.085	0.270563	0.404	0.298	0.948563	0	0	0	0	0	0
NKBA 4x240 1.00 kV	1	0.474	50	3	0	0.077	0.084	0.26738	0.308	0.295	0.939014	0	0	0	0	0	0
NKBA 4x25 1.00 kV	1	0.133	50	3	0	0.724	0.094	0.299211	2.896	0.366	1.165014	0	0	0	0	0	0
NKBA 4x300 1.00 kV	1	0.533	50	3	0	0.063	0.084	0.26738	0.252	0.289	0.919916	0	0	0	0	0	0
NKBA 4x35 1.00 kV	1	0.161	50	3	0	0.526	0.092	0.292845	2.104	0.348	1.107718	0	0	0	0	0	0
NKBA 4x50 1.00 kV	1	0.191	50	3	0	0.389	0.09	0.286479	1.556	0.332	1.056789	0	0	0	0	0	0
NKBA 4x70 1.00 kV	1	0.235	50	3	0	0.271	0.087	0.27693	1.084	0.318	1.012225	0	0	0	0	0	0
NKBA 4x95 1.00 kV	1	0.281	50	3	0	0.197	0.086	0.273747	0.788	0.307	0.977211	0	0	0	0	0	0
NKBA FOR 25.00 kV	25	0.343	50	3	0	0.128	0.122	0.388338	0	0	0	0	0	0	0	0
NKBA NOR 25.00 kV	25	0.277	50	3	0	1	1	3.183099	0	0	0	0	0	0	0	0
NYCWY 3x120/70 1.00 kV	1	0.313	50	3	0	0.157	0.072	0.229183	0.975	0.122	0.388338	0	0	0	0	0	0
NYCWY 3x150/70 1.00 kV	1	0.353	50	3	0	0.127	0.072	0.229183	0.933	0.114	0.362873	0	0	0	0	0	0
NYCWY 3x185/95 1.00 kV	1	0.399	50	3	0	0.103	0.072	0.229183	0.694	0.107	0.340592	0	0	0	0	0	0
NYCWY 3x240/120 1.00 kV	1	0.464	50	3	0	0.08	0.072	0.229183	0.545	0.104	0.331042	0	0	0	0	0	0
NYCWY 3x25/16 1.00 kV	1	0.128	50	3	0	0.724	0.08	0.254648	4.156	0.138	0.439268	0	0	0	0	0	0
NYCWY 3x300/150 1.00 kV	1	0.524	50	3	0	0.066	0.072	0.229183	0.447	0.1	0.31831	0	0	0	0	0	0
NYCWY 3x35/16 1.00 kV	1	0.157	50	3	0	0.526	0.077	0.245099	3.95	0.128	0.407437	0	0	0	0	0	0
NYCWY 3x50/25 1.00 kV	1	0.185	50	3	0	0.389	0.077	0.245099	2.56	0.12	0.381972	0	0	0	0	0	0
NYCWY 3x70/35 1.00 kV	1	0.228	50	3	0	0.271	0.074	0.235549	1.859	0.122	0.388338	0	0	0	0	0	0
NYCWY 3x95/50 1.00 kV	1	0.275	50	3	0	0.197	0.074	0.235549	1.373	0.122	0.388338	0	0	0	0	0	0
NYCWY 4x1.5/1.5 1.00 kV	1	0.026	50	3	0	12.1	0.115	0.366056	48.4	0.459	1.461042	0	0	0	0	0	0
NYCWY 4x10/10 1.00 kV	1	0.075	50	3	0	1.81	0.094	0.299211	7.24	0.378	1.203211	0	0	0	0	0	0
NYCWY 4x120/70 1.00 kV	1	0.313	50	3	0	0.157	0.08	0.254648	0.628	0.292	0.929465	0	0	0	0	0	0
NYCWY 4x150/70 1.00 kV	1	0.353	50	3	0	0.125	0.08	0.254648	0.5	0.292	0.929465	0	0	0	0	0	0
NYCWY 4x16/16 1.00 kV	1	0.098	50	3	0	1.141	0.09	0.286479	4.564	0.358	1.139549	0	0	0	0	0	0
NYCWY 4x185/95 1.00 kV	1	0.399	50	3	0	0.101	0.08	0.254648	0.404	0.292	0.929465	0	0	0	0	0	0
NYCWY 4x2.5/2.5 1.00 kV	1	0.034	50	3	0	7.28	0.11	0.350141	29.12	0.441	1.403747	0	0	0	0	0	0
NYCWY 4x240/120 1.00 kV	1	0.464	50	3	0	0.077	0.079	0.251465	0.308	0.29	0.923099	0	0	0	0	0	0
NYCWY 4x25/16 1.00 kV	1	0.128	50	3	0	0.724	0.086	0.273747	2.896	0.355	1.13	0	0	0	0	0	0
NYCWY 4x300/150 1.00 kV	1	0.524	50	3	0	0.063	0.079	0.251465	0.252	0.289	0.919916	0	0	0	0	0	0
NYCWY 4x35/16 1.00 kV	1	0.157	50	3	0	0.526	0.083	0.264197	2.104	0.314	0.999493	0	0	0	0	0	0
NYCWY 4x4/4 1.00 kV	1	0.044	50	3	0	4.56	0.107	0.340592	18.24	0.426	1.356	0	0	0	0	0	0
NYCWY 4x50/25 1.00 kV	1	0.185	50	3	0	0.389	0.083	0.264197	1.556	0.312	0.993127	0	0	0	0	0	0
NYCWY 4x6/6 1.00 kV	1	0.056	50	3	0	3.03	0.1	0.31831	12.12	0.403	1.282789	0	0	0	0	0	0
NYCWY 4x70/35 1.00 kV	1	0.228	50	3	0	0.271	0.082	0.261014	1.084	0.3	0.95493	0	0	0	0	0	0
NYCWY 4x95/50 1.00 kV	1	0.275	50	3	0	0.197	0.082	0.261014	0.788	0.299	0.951747	0	0	0	0	0	0
NYFGBY 3x120 6.00 kV	6	0.313	50	3	0	0.156	0.096	0.305577	1	1	3.183099	0	0	0	0	0	0
NYFGBY 3x150 6.00 kV	6	0.352	50	3	0	0.128	0.093	0.296028	1	1	3.183099	0	0	0	0	0	0
NYFGBY 3x185 6.00 kV	6	0.397	50	3	0	0.102	0.091	0.289662	1	1	3.183099	0	0	0	0	0	0
NYFGBY 3x240 6.00 kV	6	0.46	50	3	0	0.08	0.088	0.280113	1	1	3.183099	0	0	0	0	0	0
NYFGBY 3x25 6.00 kV	6	0.126	50	3	0	0.724	0.12	0.381972	1	1	3.183099	0	0	0	0	0	0
NYFGBY 3x300 6.00 kV	6	0.518	50	3	0	0.066	0.086	0.273747	1	1	3.183099	0	0	0	0	0	0
NYFGBY 3x35 6.00 kV	6	0.158	50	3	0	0.525	0.114	0.362873	1	1	3.183099	0	0	0	0	0	0
NYFGBY 3x50 6.00 kV	6	0.187	50	3	0	0.389	0.109	0.346958	1	1	3.183099	0	0	0	0	0	0
NYFGBY 3x70 6.00 kV	6	0.23	50	3	0	0.27	0.103	0.327859	1	1	3.183099	0	0	0	0	0	0
NYFGBY 3x95 6.00 kV	6	0.275	50	3	0	0.195	0.099	0.315127	1	1	3.183099	0	0	0	0	0	0
NYSEY 3x120 6.00 kV	6	0.284	50	3	0	0.153	0.09891	0.31484	1	1	3.183099	0	0	0	0	0	0
NYSEY 3x120 10.00 kV	10	0.312	50	3	0	0.155	0.099	0.315127	1	1	3.183099	0	0	0	0	0	0
NYSEY 3x150 6.00 kV	6	0.322	50	3	0	0.124	0.09577	0.304845	1	1	3.183099	0	0	0	0	0	0
NYSEY 3x150 10.00 kV	10	0.35	50	3	0	0.127	0.096	0.305577	1	1	3.183099	0	0	0	0	0	0
NYSEY 3x185 6.00 kV	6	0.368	50	3	0	0.0991	0.09294	0.295837	1	1	3.183099	0	0	0	0	0	0
NYSEY 3x185 10.00 kV	10	0.394	50	3	0	0.101	0.093	0.296028	1	1	3.183099	0	0	0	0	0	0
NYSEY 3x240 6.00 kV	6	0.43	50	3	0	0.0754	0.08918	0.283869	1	1	3.183099	0	0	0	0	0	0
NYSEY 3x240 10.00 kV	10	0.455	50	3	0	0.079	0.089	0.283296	1	1	3.183099	0	0	0	0	0	0
NYSEY 3x25 10.00 kV	10	0.133	50	3	0	0.723	0.127	0.404254	1	1	3.183099	0	0	0	0	0	0
NYSEY 3x300 6.00 kV	6	0.49	50	3	0	0.0601	0.08698	0.276866	1	1	3.183099	0	0	0	0	0	0
NYSEY 3x300 10.00 kV	10	0.512	50	3	0	0.064	0.087	0.27693	1	1	3.183099	0	0	0	0	0	0
NYSEY 3x35 6.00 kV	6	0.137	50	3	0	0.524	0.11995	0.381813	1	1	3.183099	0	0	0	0	0	0
NYSEY 3x35 10.00 kV	10	0.16	50	3	0	0.525	0.12	0.381972	1	1	3.183099	0	0	0	0	0	0
NYSEY 3x50 6.00 kV	6	0.165	50	3	0	0.387	0.11398	0.36281	1	1	3.183099	0	0	0	0	0	0
NYSEY 3x50 10.00 kV	10	0.189	50	3	0	0.388	0.114	0.362873	1	1	3.183099	0	0	0	0	0	0
NYSEY 3x70 6.00 kV	6	0.204	50	3	0	0.268	0.10739	0.341833	1	1	3.183099	0	0	0	0	0	0
NYSEY 3x70 10.00 kV	10	0.23	50	3	0	0.269	0.107	0.340592	1	1	3.183099	0	0	0	0	0	0
NYSEY 3x95 6.00 kV	6	0.248	50	3	0	0.193	0.10236	0.325822	1	1	3.183099	0	0	0	0	0	0
NYSEY 3x95 10.00 kV	10	0.275	50	3	0	0.194	0.102	0.324676	1	1	3.183099	0	0	0	0	0	0
NYY 3x120/70 1.00 kV	1	0.313	50	3	0	0.154	0.078	0.248282	0.96	0.347	1.104535	0	0	0	0	0	0
NYY 3x150/70 1.00 kV	1	0.353	50	3	0	0.126	0.077	0.245099	0.939	0.362	1.152282	0	0	0	0	0	0
NYY 3x185/95 1.00 kV	1	0.399	50	3	0	0.101	0.077	0.245099	0.683	0.356	1.133183	0	0	0	0	0	0
NYY 3x240/120 1.00 kV	1	0.464	50	3	0	0.078	0.076	0.241916	0.54	0.351	1.117268	0	0	0	0	0	0
NYY 3x25/16 1.00 kV	1	0.128	50	3	0	0.722	0.084	0.26738	4.144	0.395	1.257324	0	0	0	0	0	0
NYY 3x300/150 1.00 kV	1	0.524	50	3	0	0.063	0.076	0.241916	0.44	0.35	1.114085	0	0	0	0	0	0
NYY 3x35/16 1.00 kV	1	0.157	50	3	0	0.524	0.08	0.254648	3.945	0.378	1.203211	0	0	0	0	0	0
NYY 3x50/25 1.00 kV	1	0.185	50	3	0	0.388	0.082	0.261014	2.56	0.377	1.200028	0	0	0	0	0	0
NYY 3x70/35 1.00 kV	1	0.228	50	3	0	0.268	0.077	0.245099	1.832	0.353	1.123634	0	0	0	0	0	0
NYY 3x95/50 1.00 kV	1	0.275	50	3	0	0.194	0.079	0.251465	1.354	0.359	1.142733	0	0	0	0	0	0
NYY 4x1.5 1.00 kV	1	0.026	50	3	0	12.1	0.115	0.366056	48.4	0.459	1.461042	0	0	0	0	0	0
NYY 4x10 1.00 kV	1	0.075	50	3	0	1.81	0.094	0.299211	7.24	0.378	1.203211	0	0	0	0	0	0
NYY 4x120 1.00 kV	1	0.313	50	3	0	0.157	0.08	0.254648	0.628	0.292	0.929465	0	0	0	0	0	0
NYY 4x150 1.00 kV	1	0.353	50	3	0	0.125	0.08	0.254648	0.5	0.292	0.929465	0	0	0	0	0	0
NYY 4x16 1.00 kV	1	0.098	50	3	0	1.141	0.09	0.286479	4.564	0.358	1.139549	0	0	0	0	0	0
NYY 4x185 1.00 kV	1	0.399	50	3	0	0.101	0.08	0.254648	0.404	0.292	0.929465	0	0	0	0	0	0
NYY 4x2.5 1.00 kV	1	0.034	50	3	0	7.28	0.11	0.350141	29.12	0.441	1.403747	0	0	0	0	0	0
NYY 4x240 1.00 kV	1	0.464	50	3	0	0.077	0.079	0.251465	0.308	0.29	0.923099	0	0	0	0	0	0
NYY 4x25 1.00 kV	1	0.128	50	3	0	0.724	0.086	0.273747	2.896	0.355	1.13	0	0	0	0	0	0
NYY 4x300 1.00 kV	1	0.524	50	3	0	0.063	0.079	0.251465	0.252	0.289	0.919916	0	0	0	0	0	0
NYY 4x35 1.00 kV	1	0.157	50	3	0	0.526	0.083	0.264197	2.104	0.314	0.999493	0	0	0	0	0	0
NYY 4x4 1.00 kV	1	0.044	50	3	0	4.56	0.107	0.340592	18.24	0.426	1.356	0	0	0	0	0	0
NYY 4x50 1.00 kV	1	0.185	50	3	0	0.389	0.083	0.264197	1.556	0.312	0.993127	0	0	0	0	0	0
NYY 4x6 1.00 kV	1	0.056	50	3	0	3.03	0.1	0.31831	12.12	0.403	1.282789	0	0	0	0	0	0
NYY 4x70 1.00 kV	1	0.228	50	3	0	0.271	0.082	0.261014	1.084	0.3	0.95493	0	0	0	0	0	0
NYY 4x95 1.00 kV	1	0.275	50	3	0	0.197	0.082	0.261014	0.788	0.299	0.951747	0	0	0	0	0	0
PILC-AL 1x120 1.00 kV	1	0.305	50	3	0	0.253	0.09	0.286479	1	1	3.183099	0	0	0	0	0	0
PILC-AL 1x150 1.00 kV	1	0.35	50	3	0	0.206	0.088	0.280113	1	1	3.183099	0	0	0	0	0	0
PILC-AL 1x185 1.00 kV	1	0.405	50	3	0	0.164	0.086	0.273747	1	1	3.183099	0	0	0	0	0	0
PILC-AL 1x240 1.00 kV	1	0.485	50	3	0	0.125	0.084	0.26738	1	1	3.183099	0	0	0	0	0	0
PILC-AL 1x300 1.00 kV	1	0.56	50	3	0	0.1	0.083	0.264197	1	1	3.183099	0	0	0	0	0	0
PILC-AL 1x50 1.00 kV	1	0.165	50	3	0	0.641	0.107	0.340592	1	1	3.183099	0	0	0	0	0	0
PILC-AL 1x70 1.00 kV	1	0.21	50	3	0	0.443	0.097	0.308761	1	1	3.183099	0	0	0	0	0	0
PILC-AL 1x95 1.00 kV	1	0.26	50	3	0	0.32	0.093	0.296028	1	1	3.183099	0	0	0	0	0	0
PILC-AL 3x120 1.00 kV	1	0.255	50	3	0	0.253	0.068	0.216451	1	1	3.183099	0	0	0	0	0	0
PILC-AL 3x120 11.00 kV	11	0.22	50	3	0	0.253	0.083	0.264197	1	1	3.183099	0	0	0	0	0	0
PILC-AL 3x150 1.00 kV	1	0.29	50	3	0	0.206	0.069	0.219634	1	1	3.183099	0	0	0	0	0	0
PILC-AL 3x150 11.00 kV	11	0.245	50	3	0	0.206	0.082	0.261014	1	1	3.183099	0	0	0	0	0	0
PILC-AL 3x185 1.00 kV	1	0.335	50	3	0	0.164	0.068	0.216451	1	1	3.183099	0	0	0	0	0	0
PILC-AL 3x185 11.00 kV	11	0.28	50	3	0	0.164	0.08	0.254648	1	1	3.183099	0	0	0	0	0	0
PILC-AL 3x240 1.00 kV	1	0.4	50	3	0	0.125	0.068	0.216451	1	1	3.183099	0	0	0	0	0	0
PILC-AL 3x240 11.00 kV	11	0.325	50	3	0	0.125	0.078	0.248282	1	1	3.183099	0	0	0	0	0	0
PILC-AL 3x25 1.00 kV	1	0.093	50	3	0	1.2	0.076	0.241916	1	1	3.183099	0	0	0	0	0	0
PILC-AL 3x25 11.00 kV	11	0.089	50	3	0	1.2	0.105	0.334225	1	1	3.183099	0	0	0	0	0	0
PILC-AL 3x300 1.00 kV	1	0.46	50	3	0	0.1	0.067	0.213268	1	1	3.183099	0	0	0	0	0	0
PILC-AL 3x300 11.00 kV	11	0.365	50	3	0	0.1	0.076	0.241916	1	1	3.183099	0	0	0	0	0	0
PILC-AL 3x35 1.00 kV	1	0.115	50	3	0	0.868	0.074	0.235549	1	1	3.183099	0	0	0	0	0	0
PILC-AL 3x35 11.00 kV	11	0.11	50	3	0	0.868	0.098	0.311944	1	1	3.183099	0	0	0	0	0	0
PILC-AL 3x50 1.00 kV	1	0.14	50	3	0	0.641	0.083	0.264197	1	1	3.183099	0	0	0	0	0	0
PILC-AL 3x50 11.00 kV	11	0.13	50	3	0	0.641	0.094	0.299211	1	1	3.183099	0	0	0	0	0	0
PILC-AL 3x70 1.00 kV	1	0.175	50	3	0	0.443	0.071	0.226	1	1	3.183099	0	0	0	0	0	0
PILC-AL 3x70 11.00 kV	11	0.16	50	3	0	0.443	0.09	0.286479	1	1	3.183099	0	0	0	0	0	0
PILC-AL 3x95 1.00 kV	1	0.22	50	3	0	0.32	0.069	0.219634	1	1	3.183099	0	0	0	0	0	0
PILC-AL 3x95 11.00 kV	11	0.19	50	3	0	0.32	0.086	0.273747	1	1	3.183099	0	0	0	0	0	0
PILC-CU 1x120 1.00 kV	1	0.305	50	3	0	0.153	0.09	0.286479	1	1	3.183099	0	0	0	0	0	0
PILC-CU 1x150 1.00 kV	1	0.35	50	3	0	0.124	0.088	0.280113	1	1	3.183099	0	0	0	0	0	0
PILC-CU 1x185 1.00 kV	1	0.405	50	3	0	0.0991	0.086	0.273747	1	1	3.183099	0	0	0	0	0	0
PILC-CU 1x240 1.00 kV	1	0.485	50	3	0	0.0754	0.084	0.26738	1	1	3.183099	0	0	0	0	0	0
PILC-CU 1x300 1.00 kV	1	0.56	50	3	0	0.0601	0.083	0.264197	1	1	3.183099	0	0	0	0	0	0
PILC-CU 1x400 1.00 kV	1	0.65	50	3	0	0.047	0.081	0.257831	1	1	3.183099	0	0	0	0	0	0
PILC-CU 1x50 1.00 kV	1	0.165	50	3	0	0.387	0.102	0.324676	1	1	3.183099	0	0	0	0	0	0
PILC-CU 1x70 1.00 kV	1	0.21	50	3	0	0.268	0.097	0.308761	1	1	3.183099	0	0	0	0	0	0
PILC-CU 1x95 1.00 kV	1	0.26	50	3	0	0.193	0.093	0.296028	1	1	3.183099	0	0	0	0	0	0
PILC-CU 3x120 1.00 kV	1	0.325	50	3	0	0.153	0.068	0.216451	1	1	3.183099	0	0	0	0	0	0
PILC-CU 3x120 11.00 kV	11	0.28	50	3	0	0.153	0.083	0.264197	1	1	3.183099	0	0	0	0	0	0
PILC-CU 3x150 1.00 kV	1	0.375	50	3	0	0.124	0.069	0.219634	1	1	3.183099	0	0	0	0	0	0
PILC-CU 3x150 11.00 kV	11	0.315	50	3	0	0.124	0.082	0.261014	1	1	3.183099	0	0	0	0	0	0
PILC-CU 3x185 1.00 kV	1	0.43	50	3	0	0.0991	0.068	0.216451	1	1	3.183099	0	0	0	0	0	0
PILC-CU 3x185 11.00 kV	11	0.355	50	3	0	0.0991	0.08	0.254648	1	1	3.183099	0	0	0	0	0	0
PILC-CU 3x240 1.00 kV	1	0.51	50	3	0	0.0754	0.068	0.216451	1	1	3.183099	0	0	0	0	0	0
PILC-CU 3x240 11.00 kV	11	0.41	50	3	0	0.0754	0.078	0.248282	1	1	3.183099	0	0	0	0	0	0
PILC-CU 3x25 1.00 kV	1	0.12	50	3	0	0.727	0.076	0.241916	1	1	3.183099	0	0	0	0	0	0
PILC-CU 3x25 11.00 kV	11	0.115	50	3	0	0.727	0.105	0.334225	1	1	3.183099	0	0	0	0	0	0
PILC-CU 3x300 1.00 kV	1	0.59	50	3	0	0.0601	0.067	0.213268	1	1	3.183099	0	0	0	0	0	0
PILC-CU 3x300 11.00 kV	11	0.46	50	3	0	0.0601	0.076	0.241916	1	1	3.183099	0	0	0	0	0	0
PILC-CU 3x35 1.00 kV	1	0.15	50	3	0	0.524	0.074	0.235549	1	1	3.183099	0	0	0	0	0	0
PILC-CU 3x35 11.00 kV	11	0.14	50	3	0	0.524	0.098	0.311944	1	1	3.183099	0	0	0	0	0	0
PILC-CU 3x400 1.00 kV	1	0.68	50	3	0	0.047	0.067	0.213268	1	1	3.183099	0	0	0	0	0	0
PILC-CU 3x400 11.00 kV	11	0.52	50	3	0	0.047	0.075	0.238732	1	1	3.183099	0	0	0	0	0	0
PILC-CU 3x50 1.00 kV	1	0.18	50	3	0	0.387	0.073	0.232366	1	1	3.183099	0	0	0	0	0	0
PILC-CU 3x50 11.00 kV	11	0.165	50	3	0	0.387	0.094	0.299211	1	1	3.183099	0	0	0	0	0	0
PILC-CU 3x70 1.00 kV	1	0.23	50	3	0	0.268	0.071	0.226	1	1	3.183099	0	0	0	0	0	0
PILC-CU 3x70 11.00 kV	11	0.205	50	3	0	0.268	0.09	0.286479	1	1	3.183099	0	0	0	0	0	0
PILC-CU 3x95 1.00 kV	1	0.28	50	3	0	0.193	0.069	0.219634	1	1	3.183099	0	0	0	0	0	0
PILC-CU 3x95 11.00 kV	11	0.245	50	3	0	0.193	0.086	0.273747	1	1	3.183099	0	0	0	0	0	0
PVC-SWA-AL 2x16 1.00 kV	1	0.071	50	3	0	1.89	0.086	0.273747	1	1	3.183099	0	0	0	0	0	0
PVC-SWA-AL 2x25 1.00 kV	1	0.094	50	3	0	1.2	0.085	0.270563	1	1	3.183099	0	0	0	0	0	0
PVC-SWA-AL 2x35 1.00 kV	1	0.115	50	3	0	0.868	0.082	0.261014	1	1	3.183099	0	0	0	0	0	0
PVC-SWA-AL 2x50 1.00 kV	1	0.139	50	3	0	0.641	0.082	0.261014	1	1	3.183099	0	0	0	0	0	0
PVC-SWA-AL 2x70 1.00 kV	1	0.175	50	3	0	0.443	0.079	0.251465	1	1	3.183099	0	0	0	0	0	0
PVC-SWA-AL 2x95 1.00 kV	1	0.211	50	3	0	0.32	0.078	0.248282	1	1	3.183099	0	0	0	0	0	0
PVC-SWA-AL 3x120 1.00 kV	1	0.216	50	3	0	0.253	0.077	0.245099	1	1	3.183099	0	0	0	0	0	0
PVC-SWA-AL 3x150 1.00 kV	1	0.25	50	3	0	0.206	0.077	0.245099	1	1	3.183099	0	0	0	0	0	0
PVC-SWA-AL 3x16 1.00 kV	1	0.061	50	3	0	1.89	0.086	0.273747	1	1	3.183099	0	0	0	0	0	0
PVC-SWA-AL 3x185 1.00 kV	1	0.287	50	3	0	0.164	0.077	0.245099	1	1	3.183099	0	0	0	0	0	0
PVC-SWA-AL 3x240 1.00 kV	1	0.342	50	3	0	0.125	0.076	0.241916	1	1	3.183099	0	0	0	0	0	0
PVC-SWA-AL 3x25 1.00 kV	1	0.08	50	3	0	1.2	0.085	0.270563	1	1	3.183099	0	0	0	0	0	0
PVC-SWA-AL 3x300 1.00 kV	1	0.399	50	3	0	0.1	0.076	0.241916	1	1	3.183099	0	0	0	0	0	0
PVC-SWA-AL 3x35 1.00 kV	1	0.99	50	3	0	0.868	0.082	0.261014	1	1	3.183099	0	0	0	0	0	0
PVC-SWA-AL 3x50 1.00 kV	1	0.119	50	3	0	0.641	0.082	0.261014	1	1	3.183099	0	0	0	0	0	0
PVC-SWA-AL 3x70 1.00 kV	1	0.151	50	3	0	0.443	0.079	0.251465	1	1	3.183099	0	0	0	0	0	0
PVC-SWA-AL 3x95 1.00 kV	1	0.186	50	3	0	0.32	0.078	0.248282	1	1	3.183099	0	0	0	0	0	0
PVC-SWA-CU 1x120 1.00 kV	1	0.383	50	3	0	0.153	0.099	0.315127	1	1	3.183099	0	0	0	0	0	0
PVC-SWA-CU 1x150 1.00 kV	1	0.436	50	3	0	0.124	0.097	0.308761	1	1	3.183099	0	0	0	0	0	0
PVC-SWA-CU 1x185 1.00 kV	1	0.49	50	3	0	0.0991	0.095	0.302394	1	1	3.183099	0	0	0	0	0	0
PVC-SWA-CU 1x240 1.00 kV	1	0.566	50	3	0	0.0754	0.093	0.296028	1	1	3.183099	0	0	0	0	0	0
PVC-SWA-CU 1x300 1.00 kV	1	0.616	50	3	0	0.0601	0.091	0.289662	1	1	3.183099	0	0	0	0	0	0
PVC-SWA-CU 1x400 1.00 kV	1	0.674	50	3	0	0.047	0.091	0.289662	1	1	3.183099	0	0	0	0	0	0
PVC-SWA-CU 1x50 1.00 kV	1	0.23	50	3	0	0.387	0.109	0.346958	1	1	3.183099	0	0	0	0	0	0
PVC-SWA-CU 1x70 1.00 kV	1	0.286	50	3	0	0.268	0.104	0.331042	1	1	3.183099	0	0	0	0	0	0
PVC-SWA-CU 1x95 1.00 kV	1	0.338	50	3	0	0.0193	0.1	0.31831	1	1	3.183099	0	0	0	0	0	0
PVC-SWA-CU 2x120 1.00 kV	1	0.335	50	3	0	0.153	0.076	0.241916	1	1	3.183099	0	0	0	0	0	0
PVC-SWA-CU 2x150 1.00 kV	1	0.38	50	3	0	0.124	0.076	0.241916	1	1	3.183099	0	0	0	0	0	0
PVC-SWA-CU 2x16 1.00 kV	1	0.097	50	3	0	1.15	0.088	0.280113	1	1	3.183099	0	0	0	0	0	0
PVC-SWA-CU 2x185 1.00 kV	1	0.44	50	3	0	0.0991	0.076	0.241916	1	1	3.183099	0	0	0	0	0	0
PVC-SWA-CU 2x240 1.00 kV	1	0.52	50	3	0	0.0754	0.075	0.238732	1	1	3.183099	0	0	0	0	0	0
PVC-SWA-CU 2x25 1.00 kV	1	0.13	50	3	0	0.727	0.083	0.264197	1	1	3.183099	0	0	0	0	0	0
PVC-SWA-CU 2x300 1.00 kV	1	0.59	50	3	0	0.0601	0.075	0.238732	1	1	3.183099	0	0	0	0	0	0
PVC-SWA-CU 2x35 1.00 kV	1	0.16	50	3	0	0.524	0.081	0.257831	1	1	3.183099	0	0	0	0	0	0
PVC-SWA-CU 2x400 1.00 kV	1	0.67	50	3	0	0.047	0.074	0.235549	1	1	3.183099	0	0	0	0	0	0
PVC-SWA-CU 2x50 1.00 kV	1	0.19	50	3	0	0.387	0.081	0.257831	1	1	3.183099	0	0	0	0	0	0
PVC-SWA-CU 2x70 1.00 kV	1	0.235	50	3	0	0.268	0.079	0.251465	1	1	3.183099	0	0	0	0	0	0
PVC-SWA-CU 2x95 1.00 kV	1	0.29	50	3	0	0.193	0.077	0.245099	1	1	3.183099	0	0	0	0	0	0
PVC-SWA-CU 3x120 1.00 kV	1	0.29	50	3	0	0.153	0.076	0.241916	1	1	3.183099	0	0	0	0	0	0
PVC-SWA-CU 3x150 1.00 kV	1	0.335	50	3	0	0.124	0.076	0.241916	1	1	3.183099	0	0	0	0	0	0
PVC-SWA-CU 3x16 1.00 kV	1	0.083	50	3	0	1.15	0.088	0.280113	1	1	3.183099	0	0	0	0	0	0
PVC-SWA-CU 3x185 1.00 kV	1	0.38	50	3	0	0.0991	0.076	0.241916	1	1	3.183099	0	0	0	0	0	0
PVC-SWA-CU 3x240 1.00 kV	1	0.45	50	3	0	0.0754	0.075	0.238732	1	1	3.183099	0	0	0	0	0	0
PVC-SWA-CU 3x25 1.00 kV	1	0.11	50	3	0	0.727	0.083	0.264197	1	1	3.183099	0	0	0	0	0	0
PVC-SWA-CU 3x300 1.00 kV	1	0.51	50	3	0	0.0601	0.075	0.238732	1	1	3.183099	0	0	0	0	0	0
PVC-SWA-CU 3x35 1.00 kV	1	0.135	50	3	0	0.524	0.081	0.257831	1	1	3.183099	0	0	0	0	0	0
PVC-SWA-CU 3x400 1.00 kV	1	0.59	50	3	0	0.047	0.074	0.235549	1	1	3.183099	0	0	0	0	0	0
PVC-SWA-CU 3x50 1.00 kV	1	0.165	50	3	0	0.387	0.081	0.257831	1	1	3.183099	0	0	0	0	0	0
PVC-SWA-CU 3x70 1.00 kV	1	0.205	50	3	0	0.268	0.079	0.251465	1	1	3.183099	0	0	0	0	0	0
PVC-SWA-CU 3x95 1.00 kV	1	0.25	50	3	0	0.193	0.077	0.245099	1	1	3.183099	0	0	0	0	0	0
XHIV 1x185 20.00 kV	20	0.4	50	3	0	0.1	0.12085	0.384677	1	1	3.183099	0	0	0	0	0	0
XLPE-CU 3x120 11.00 kV	11	0.335	50	3	0	0.153	0.097	0.308761	1	1	3.183099	0	0	0	0	0	0
XLPE-CU 3x150 11.00 kV	11	0.375	50	3	0	0.124	0.094	0.299211	1	1	3.183099	0	0	0	0	0	0
XLPE-CU 3x185 11.00 kV	11	0.42	50	3	0	0.0991	0.092	0.292845	1	1	3.183099	0	0	0	0	0	0
XLPE-CU 3x240 11.00 kV	11	0.485	50	3	0	0.0754	0.089	0.283296	1	1	3.183099	0	0	0	0	0	0
XLPE-CU 3x25 11.00 kV	11	0.145	50	3	0	0.727	0.124	0.394704	1	1	3.183099	0	0	0	0	0	0
XLPE-CU 3x300 11.00 kV	11	0.54	50	3	0	0.0601	0.086	0.273747	1	1	3.183099	0	0	0	0	0	0
XLPE-CU 3x35 11.00 kV	11	0.17	50	3	0	0.524	0.116	0.369239	1	1	3.183099	0	0	0	0	0	0
XLPE-CU 3x50 11.00 kV	11	0.205	50	3	0	0.387	0.111	0.353324	1	1	3.183099	0	0	0	0	0	0
XLPE-CU 3x70 11.00 kV	11	0.245	50	3	0	0.268	0.106	0.337408	1	1	3.183099	0	0	0	0	0	0
XLPE-CU 3x95 11.00 kV	11	0.295	50	3	0	0.193	0.1	0.31831	1	1	3.183099	0	0	0	0	0	0
ZEBRA 1x300 150.00 kV	150	0.5	50	3	0	0.06079	0.4178	1.329899	1	1	3.183099	0	0	0	0	0	0

## Wires
Size	Stranding	Material	Diameter [cm]	GMR [m]	R [Ohm/km]	Rating [A]
1	-	ACSR	0.902	0.001274	0.857492	200
1	7 STRD	Copper	0.833	0.003024	0.475349	270
1	CLASS A	AA	0.833	0.003021	0.760558	177
2	6/1	ACSR	0.803	0.001274	1.050117	180
2	7 STRD	Copper	0.742	0.002691	0.599002	230
2	7/1	ACSR	0.826	0.001536	1.025262	180
2	AWG SLD	Copper	0.655	0.002548	0.587196	220
2	CLASS A	AA	0.742	0.002691	0.957533	156
3	6/1	ACSR	0.714	0.001311	1.286238	160
3	AWG SLD	Copper	0.582	0.002271	0.740674	190
4	6/1	ACSR	0.635	0.001332	1.596924	140
4	7/1	ACSR	0.653	0.001378	1.584497	140
4	AWG SLD	Copper	0.518	0.002021	0.933921	170
4	CLASS A	AA	0.589	0.002134	1.524224	90
5	6/1	ACSR	0.566	0.001268	1.975960	120
5	AWG SLD	Copper	0.462	0.001798	1.177498	140
6	6/1	ACSR	0.503	0.001201	2.473057	100
6	AWG SLD	Copper	0.411	0.001603	1.485077	120
6	CLASS A	AA	0.467	0.001692	2.425212	65
7	AWG SLD	Copper	0.367	0.001426	1.870327	110
8	AWG SLD	Copper	0.326	0.001268	2.361211	90
9	AWG SLD	Copper	0.291	0.001131	2.905407	80
10	AWG SLD	Copper	0.259	0.001006	3.667706	75
12	AWG SLD	Copper	0.205	0.000799	5.825169	40
14	AWG SLD	Copper	0.163	0.000634	9.241157	20
16	AWG SLD	Copper	0.129	0.000500	14.742777	10
18	AWG SLD	Copper	0.102	0.000396	23.408669	5
19	AWG SLD	Copper	0.091	0.000354	29.521532	4
20	AWG SLD	Copper	0.081	0.000314	37.085919	3
22	AWG SLD	Copper	0.064	0.000250	59.330697	2
24	AWG SLD	Copper	0.051	0.000198	94.209816	1
1/0	-	ACSR	1.011	0.001359	0.695936	230
1/0	7 STRD	Copper	0.935	0.003392	0.377172	310
1/0	CLASS A	AA	0.935	0.003383	0.602730	202
2/0	-	ACSR	1.135	0.001554	0.556127	270
2/0	7 STRD	Copper	1.052	0.003816	0.298880	360
2/0	CLASS A	AA	1.052	0.003810	0.477834	230
3/0	12 STRD	Copper	1.250	0.004752	0.237364	420
3/0	6/1	ACSR	1.275	0.001829	0.449251	300
3/0	7 STRD	Copper	1.179	0.004279	0.237364	420
3/0	CLASS A	AA	1.179	0.004267	0.379658	263
3/8	INCH STE	Steel	0.953	0.000003	2.671896	150
4/0	12 STRD	Copper	1.402	0.005334	0.188275	490
4/0	19 STRD	Copper	1.341	0.005084	0.188275	480
4/0	6/1	ACSR	1.430	0.002481	0.367852	340
4/0	7 STRD	Copper	1.326	0.004813	0.188275	480
4/0	CLASS A	AA	1.326	0.004816	0.300744	299
250,000	12 STRD	Copper	1.524	0.005797	0.159692	540
250,000	19 STRD	Copper	1.458	0.005526	0.159692	540
250,000	CON LAY	AA	1.440	0.005212	0.254762	329
266,800	26/7	ACSR	1.631	0.006614	0.239228	460
266,800	CLASS A	AA	1.488	0.005395	0.238607	320
300,000	12 STRD	Copper	1.669	0.006340	0.133595	610
300,000	19 STRD	Copper	1.598	0.006056	0.133595	610
300,000	26/7	ACSR	1.727	0.007010	0.212509	490
300,000	30/7	ACSR	1.778	0.007346	0.212509	500
300,000	CON LAY	AA	1.598	0.006035	0.212509	350
336,400	26/7	ACSR	1.831	0.007437	0.190140	530
336,400	30/7	ACSR	1.882	0.007772	0.190140	530
336,400	CLASS A	AA	1.692	0.006401	0.189518	410
350,000	12 STRD	Copper	1.803	0.006858	0.114643	670
350,000	19 STRD	Copper	1.725	0.006523	0.114643	670
350,000	CON LAY	AA	1.725	0.006523	0.182683	399
397,500	26/7	ACSR	1.989	0.008077	0.160935	590
397,500	30/7	ACSR	2.047	0.008473	0.160935	600
397,500	CLASS A	AA	1.839	0.006949	0.160314	440
400,000	19 STRD	Copper	1.844	0.006980	0.100600	730
450,000	19 STRD	Copper	1.956	0.007407	0.089664	780
450,000	CON LAG	AA	1.956	0.007407	0.142294	450
477,000	26/7	ACSR	2.179	0.008839	0.134216	670
477,000	30/7	ACSR	2.243	0.009266	0.134216	670
477,000	CLASS A	AA	2.019	0.007742	0.134216	510
500,000	19 STRD	Copper	2.060	0.007803	0.080965	840
500,000	37 STRD	Copper	2.068	0.007925	0.080965	840
500,000	CON LAY	AA	2.065	0.007925	0.128002	483
556,500	26/7	ACSR	2.355	0.009540	0.115513	730
556,500	30/7	ACSR	2.421	0.009997	0.115513	730
556,500	CLASS A	AA	2.179	0.008382	0.115575	560
600,000	37 STRD	Copper	2.263	0.008687	0.068040	940
600,000	CON LAY	AA	2.263	0.008687	0.106876	520
605,000	26/7	ACSR	2.454	0.009967	0.106876	760
605,000	54/7	ACSR	2.421	0.009784	0.110293	750
636,000	27/7	ACSR	2.515	0.010211	0.100538	780
636,000	30/19	ACSR	2.588	0.010698	0.100538	780
636,000	54/7	ACSR	2.482	0.010028	0.104887	770
636,000	CLASS A	AA	2.332	0.008961	0.101284	620
666,600	54/7	ACSR	2.540	0.010272	0.099482	800
700,000	37 STRD	Copper	2.446	0.009388	0.058844	1040
700,000	CON LAY	AA	2.446	0.009388	0.091963	580
715,500	26/7	ACSR	2.670	0.010820	0.089602	840
715,500	30/19	ACSR	2.746	0.011339	0.089602	840
715,500	54/7	ACSR	2.631	0.010638	0.092087	830
715,500	CLASS A	AA	2.474	0.009510	0.090099	680
750,000	37 STRD	AA	2.532	0.009723	0.055178	1090
750,000	CON LAY	AA	2.532	0.009723	0.086371	602
795,000	26/7	ACSR	2.814	0.011430	0.080033	900
795,000	30/19	ACSR	2.896	0.011979	0.080033	910
795,000	54/7	ACSR	2.776	0.011217	0.085625	900
795,000	CLASS A	AA	2.606	0.009997	0.081400	720