## Control modes
				Variable				Constant
Devices	r	x	B	Gsw	k	m	Ɵ	Beq		Zero constraint	Vf	Vt	Pf	Qt	Comment	Fixed Var1	Fixed Var2
Line	Param	Param	Param	0	1	1	0	0					Line, series reactor etc.	-	-
Transformer 0	Param	Param	Param	0	1	Param	Param	0					Fixed transformer	-	-
Transformer 1	Param	Param	Param	0	1	Param	Var	0					Transformer with power control and no voltage control	Pf	-
Transformer 2	Param	Param	Param	0	1	Var	Param	0					Transformer with voltage control	Vf or Vt	-
Transformer 3	Param	Param	Param	0	1	Var	Var	0					Transformer with voltage and power control	Pf	Vf or Vt
				1
VSC 1	Param	Param	0	f(I)	√3/2	Var	Param	Var		Si		si			AC voltage control (voltage “to”)	Theta	Vac (Vt)
VSC 2	Param	Param	0	f(I)	√3/2	Param	Var	Var		Si			si	si	Active and reactive power control	Pf	Qac (Qt)
VSC 3	Param	Param	0	f(I)	√3/2	Var	Var	Var		Si		si	si		Active power and AC voltage control	Pf	Vac (Vt)
VSC 4	Param	Param	0	f(I)	√3/2	Var	Param	Var		No	si			si	Dc voltage and Reactive power flow control	Vdc (Vf)	Qac (Qt)
VSC 5	Param	Param	0	f(I)	√3/2	Var	Param	Var		No	si	si			Ac and Dc voltage control	Vdc (Vf)	Vac (Vt)
VSC 6	Param	Param	0	f(I)	√3/2	Var	Param	Var					Dc voltage droop and reactive power flow control	Vdc droop	Qac (Qt)
VSC 7	Param	Param	0	f(I)	√3/2	Var	Param	Var					Dc voltage droop and Ac voltage control	Vdc droop	Vac (Vt)

				g(x)	x	Indices	Modes
				Re(gs)	Va	pvpq	-
				Im(Gs)	Vm	pq	-
				Re(Sf) – Pset	Theta	sh
				Im(Sf)	Beq	qz
				Im(St) - Qset	Beq	qt
				Im(Gs)[f]	m	vf
				Im(Gs)[t]	m	vt

	Control active power flow	Force the reactive power flow at the “from” side to be Zero	Control the Voltage “from”	Control the voltage “to”	Control the reactive power flow
	Ish	Iqz	Ivf	Ivt	Iqt
VSC 1	0	1	0	1	0	AC voltage control (voltage “to”)
VSC 2	1	1	0	0	1	Active and reactive power control
VSC 3	1	1	0	1	0	Active power and AC voltage control
VSC 4	0	0	1	0	1	Dc voltage and Reactive power flow control
VSC 5	0	0	1	1	0	Ac and Dc voltage control
VSC 6					Dc voltage droop and reactive power flow control
VSC 7					Dc voltage droop and Ac voltage control
Transformer 0	0	0	0	0	0	Fixed transformer
Transformer 1	1	0	0	0	0	Phase shifter → controls power
Transformer 2	0	0	1	0	0	Control the voltage at the “from” side
Transformer 3	0	0	0	1	0	Control the voltage at the “to” side
Transformer 4	1	0	1	0	0	Control the power flow and the voltage at the “from” side
Transformer 5	1	0	0	1	0	Control the power flow and the voltage at the “to” side

## Sheet2
		VSC1	VSC2	VSC3	VSC4	VSC5
DC	Vm(from)				Const.	Const.
AC	Vm(to)	Const.		Const.		Const.
DC	Va(from)
AC	Va(to)
DC	Pf		Const.	Const.
AC	Pt
DC	Qf		Const.
AC	Qt				Const.
-	m		Const.
-	Ɵsh	Const.
-	Beq

Equations		Variables

gp = ∆P = 0		Va
gq = ∆Q = 0		Vm
gsh = Pf – Pf_set		Ɵsh
gqz = Qf = 0		Beq
gvf = ∆Q = 0		m
gvt = ∆Q = 0		m
gqt = Qt - Qt_set		Beq

## Vars table (final)
mismatch	∆Pf	Qf	Qbus @f	Qbus @t	∆Qt
Modified variable	Ɵsh	Beq	m	m	Beq
Controlled variable	Pf (Pdc)	Qf (Qdc)	Vf (Vdc)	Vt (Vac)	Qt (Qac)
Indices	Ish	Iqz	Ivf	Ivt	Iqt
VSC 1	-	1	-	1	-	AC voltage control (voltage “to”)
VSC 2	1	1	-	-	1	Active and reactive power control
VSC 3	1	1	-	1	-	Active power and AC voltage control
VSC 4	-	-	1	-	1	Dc voltage and Reactive power flow control
VSC 5	-	-	-	1	1	Ac and Dc voltage control
Transformer 0	-	-	-	-	-	Fixed transformer
Transformer 1	1	-	-	-	-	Phase shifter → controls power
Transformer 2	-	-	1	-	-	Control the voltage at the “from” side
Transformer 3	-	-	-	1	-	Control the voltage at the “to” side
Transformer 4	1	-	1	-	-	Control the power flow and the voltage at the “from” side
Transformer 5	1	-	-	1	-	Control the power flow and the voltage at the “to” side